Copyright 2019 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 210548 - VIBRATION AND SEISMIC CONTROLS FOR FIRE-SUPPRESSION PIPING AND EQUIPMENT

Use this Section if Project is in a seismic area. Use Section 210548.13 "Vibration Controls for Fire-Suppression Piping and Equipment" for projects not in a seismic area.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Elastomeric isolation pads.

          - Elastomeric isolation mounts.

          - Restrained elastomeric isolation mounts.

          - Elastomeric hangers.

          - Snubbers.

          - Seismic Restraints - rigid type.

          - Seismic Restraints - cable type.

          - Seismic Restraint accessories.

          - Post-installed concrete anchors.

          - Concrete inserts.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment" for devices for plumbing equipment and systems.

          - Section 230548 "Vibration and Seismic Controls for HVAC" for devices for HVAC equipment and systems.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - ASCE: American Society of Civil Engineers.

        - Designated Seismic System: A fire-suppression component that requires design in accordance with ASCE/SEI 7, Ch. 13 and for which the Component Importance Factor is greater than 1.0.

        - FM: Factory Mutual.

        - IBC: International Building Code.

        - ICC-ES: International Code Council Evaluation Services.

        - NRTL: Nationally recognized testing laboratory.

        - OPA: OSHPD Preapproval of anchorage number, Office of Statewide Health Planning & Development (for the State of California owned and regulated medical facilities).

        - OPM: Manufacturer’s Preapproval Certification Number (for the State of California owned and regulated medical facilities).

        - OSHPD: Office of Statewide Health Planning and Development (for the State of California).

        - UL: Underwriters Laboratories.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include rated load, rated deflection, and overload capacity for each vibration isolation device.

          - Include Load Rating for each seismic restraint fitting or assembly and prying factor for each seismic restraint structure attachment fitting

          - Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of vibration isolation device and seismic-[ and wind-load-]restraint component.

See the Evaluations for a discussion on seismic-restraint capacities and rating services. Retain all options in first subparagraph below that apply.

          - Annotate types and sizes of seismic restraints and accessories, complete with listing markings or report numbers and load rating in tension and compression as evaluated by [ICC-ES product listing] [UL product listing] [FM Approvals] [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

          - Annotate to indicate application of each product submitted and compliance with requirements.

          - Interlocking Snubbers: Include ratings for horizontal, vertical, and combined loads.

        - Shop Drawings:

          - Detail fabrication and assembly of equipment bases. Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting.

          - Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting.

Retain "Delegated Design Submittal" Paragraph below if design services have been delegated to Contractor.

        - Delegated Design Submittal:

          - For each seismic-restraint [and] [wind-load protection] device, including [seismic-restrained mounting,] [pipe-riser support,] [snubber,] [seismic restraint,] [seismic-restraint accessory,] [and] [concrete anchor and insert] that is required by this Section or is indicated on Drawings, submit the following:

            - Seismic-[ and Wind-Load-]Restraint Selection: Select seismic [and wind-load ]restraints complying with performance requirements, design criteria, and analysis data.

            - Riser Supports: Include riser supports complying with [NFPA 13-16 for 2018 IBC] [NFPA 13-19 for most recent edition] <Insert NFPA 13 Edition>.

            - Post-Installed Concrete Anchors and Inserts: Include calculations showing anticipated seismic[ and wind] loads. Include certification that device is approved by an NRTL for seismic applications.

Retain "Seismic Design Calculations" Subparagraph below if seismic design services have been delegated to Contractor.

            - Seismic Design Calculations: Submit all input data and loading calculations prepared under "Seismic Design Calculations" Paragraph in "Performance Requirements" Article.

Retain "Wind-Load Design Calculations" Subparagraph below if wind-load design services have been delegated to Contractor.

            - Wind-Load Design Calculations: Submit all static and dynamic loading calculations prepared under "Wind-Load Design Calculations" in "Performance Requirements" Article.

            - Qualified Professional Engineer: All designated-design submittals for seismic [and wind-load-restraint ]calculations are to be signed and sealed by qualified professional engineer responsible for their preparation.

Retain first subparagraph below only if design requirements apply but calculations have not been made and details or charts on Drawings do not describe seismic or wind restraints in detail. Retaining below requires Contractor to submit seismic restraint delegated design Drawings prepared by a professional engineer. Revise to suit Project requirements.

          - Seismic-[ and Wind-Load-]Restraint Detail Drawing:

            - Design Analysis: To support selection and arrangement of seismic[ and wind] restraints. Include calculations of combined tensile and shear loads.

            - Details: Indicate fabrication and arrangement. Detail attachments of restraints to restrained items and to the structure. Show attachment locations, methods, and spacings. Identify components, list their strengths, and indicate directions and values of forces transmitted to the structure during seismic events. Indicate association with vibration isolation devices.

Retain first subparagraph below if Project includes equipment mounted outdoors or otherwise subject to wind loading.

            - Coordinate seismic restraint details with wind-load restraint details required for equipment mounted outdoors. Comply also with requirements in other Sections for equipment mounted outdoors.

          - Product Listing, Preapproval, and Evaluation Documentation: By [an evaluation service member of ICC-ES] [UL] [FM Approvals] [OSHPD] [an agency acceptable to authorities having jurisdiction], showing maximum ratings of restraint items and the basis for approval (tests or calculations).

          - All delegated design submittals for seismic-[ and wind-load-]restraint detail Drawings are to be signed and sealed by qualified professional engineer responsible for their preparation.

      - INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

        - Coordination Drawings: Show coordination of seismic bracing for fire-suppression piping and equipment with other systems and equipment in the vicinity, including other supports and restraints, if any.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For [professional engineer] [and] [testing agency].

Retain "Welding certificates" Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Assurance" Article.

        - Welding certificates.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

Retain "Seismic Qualification Data" Paragraph below in "Informational Submittals" Article of all Specification Sections that specify Designated Seismic Systems, or as required by authorities having jurisdiction.

See "Special Certification" Article in the Evaluations for a discussion on certification and see Paragraph 13.2.2 of ASCE/SEI 7-16 for specific requirements. Fire-suppression system engineer must identify all equipment and systems required to have special certification. These must be identified in Equipment Schedule or separate Vibration Isolation, Seismic, and Wind-Load-Restraints Schedule; or, if the number of devices and systems is small, they can be listed in the Specifications.

        - Special Certification of Designated Seismic Systems: Provide special certification for all Designated Seismic Systems assigned to Seismic Design Categories C through F. Designated Seismic Systems include:

          - All active nonstructural mechanical equipment that must remain operable following the design earthquake ground motion. This equipment is assigned a Component Importance Factor greater than 1.0.

          - Components with hazardous substances and assigned a Component Importance Factor of 1.5.

        - Provide Special Certification of Designated Seismic Systems:

          - Provide equipment manufacturer's written certification for each designated active fire-suppression system component, stating that it will remain operable following the design earthquake. Certification must be based on requirements of ASCE/SEI 7, including shake table testing per ICC-ES AC156 or a similar nationally recognized testing standard procedure acceptable to authorities having jurisdiction.

            - Active fire-suppression designated seismic systems are those with parts that rotate, move mechanically, or are energized during operation unless they are considered rugged.

            - Fire-suppression components that contain motors of greater than 10 hp or have a thermal exchange greater than 200 MBH are not rugged.

            - Fire-suppression piping and ductwork is not active and does not require AC 156 shake table testing.

            - Fire-suppression active designated seismic systems for which experience data for seismic qualification that are acceptable to authorities having jurisdiction does not require AC 156 shake table testing.

          - Provide equipment manufacturer's written certification that components with hazardous contents maintain containment following the design earthquake by methods required in ASCE/SEI 7-16.

          - Submit evidence demonstrating compliance with these requirements for approval to authorities having jurisdiction after review and acceptance by a licensed professional engineer.

Retain subparagraph below only if Designated Seismic Systems are not scheduled. If a schedule is not being used, all Designated Seismic Systems must be listed below. See "Special Certification" Article in the Evaluations for more information.

          - The following fire-suppression system systems and components are Designated Seismic Systems and require written special certification of seismic qualification by manufacturer:

            - <Insert list>.

Retain "Wind-Load Performance Certification" Paragraph below in "Informational Submittals" Article of all Specification Sections that specify fire-suppression system equipment requiring wind-load certification.

See "Wind-Load Certification" Article in the Evaluations for a discussion on certification. Certification requirement covers fire-suppression system equipment subject to wind load. These must be identified by fire-suppression system engineer in the Equipment Schedule or separate Vibration Isolation, Seismic, and Wind-Load-Restraints Schedule; or, if the number of devices and systems is small, they can be listed in the Specifications.

        - Wind-Load Performance Certification: Provide special certification for fire-suppression system components subject to high-wind exposure and impact damage and designated on Drawings or in the Specifications to require wind-load performance certification.

          - Provide equipment manufacturer's written certification for each designated fire-suppression system device, stating that it will remain in place and operable following the design wind event and comply with all requirements of authorities having jurisdiction.

          - Certification must be based on ICC-ES or similar nationally recognized testing standard procedures acceptable to authorities having jurisdiction

Retain subparagraph below only if systems requiring wind-load performance certification are not scheduled on Drawings. If a schedule is not included on Drawings, all wind-force performance certified systems must be listed below. See "Wind-Load Certification" Article in the Evaluations for more information.

          - The following fire-suppression system systems and components require special certification for high wind performance. Written special certification of resistance to the effects of high wind load and impact damage must be provided by manufacturer.

            - <Insert list>.

      - QUALITY ASSURANCE

If an independent testing agency is required, see Section 014000 "Quality Requirements" for general testing and inspecting agency qualification requirements. If additional control is needed, retain "Testing Agency Qualifications" Paragraph below to specify 29 CFR 1910.7 that defines "NRTL" (nationally recognized testing laboratory) as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that comply with certain OSHA criteria.

Retain below if Contractor is to select testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.

        - Testing Agency Qualifications: An independent agency, with the experience and capability to conduct testing indicated, that is an NRTL as defined by OSHA in 29 CFR 1910.7 and that is acceptable to authorities having jurisdiction.

        - Comply with seismic-restraint[ and wind load] requirements of all applicable codes and authorities having jurisdiction unless requirements in this Section are more stringent.

        - Comply with the requirements of [NFPA 13-16 for 2018 IBC] [NFPA 13-19 for most recent edition] <Insert NFPA 13 Edition> and ASCE/SEI 7-16 for anchorage to concrete, including the effects of prying, unless the requirements of the applicable edition of the IBC or this Section are more stringent.

          - Overstrength value for determining concrete anchor capacity in ASCE/SEI 7-16, need not be taken as greater than 2.0.

        - Do not use power-actuated fasteners in concrete or steel for hanging or bracing in Seismic Design Category D, E, or F nor in masonry in any Seismic Design Category, unless approved for seismic loading and satisfy the requirements of [ [NFPA 13-16 for 2018 IBC] [NFPA 13-19 for most recent edition] <Insert NFPA 13 Edition>.

        - Comply with requirements of [NFPA 13-16 for 2018 IBC] [NFPA 13-19 for most recent edition] <Insert NFPA 13 Edition> and ASCE 19-16 for 2018 IBC for steel cable assemblies used for Seismic Restraints-Cable Type.

        - Friction Clips:

        - Component attachments shall be bolted, welded, or otherwise positively fastened without consideration of friction resistance resulting from the effects of gravity. Friction clips (C-Type beam clamps) shall not be used in Seismic Design Category D, E, or F to support permanent loads in addition to seismic loads. C-type clamps are permitted for fastening 156 hangers, when they are equipped with retaining straps, equivalent to those specified in NFPA 13, and locknuts are provide to prevent loosening of threaded connections.

Retain "Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

        - Welding Qualifications: Qualify procedures and personnel in accordance with AWS D1.1/D1.1M, "Structural Welding Code - Steel."

        - Seismic-[ and Wind-Load-]Restraint Device Load Ratings: Devices to be tested and rated in accordance with applicable code requirements and authorities having jurisdiction. Devices to be listed by a nationally recognized third party that requires periodic follow-up inspections and has a listing directory available to the public. Provide third-party listing by one or more of the following: [ICC-ES product listing] [UL product listing] [FM Approvals] [an evaluation service member of ICC-ES] [an agency acceptable to authorities having jurisdiction].

        - Seismic restraint devices shall have load ratings based on testing conducted in accordance with the IBC referenced standards and listed by a nationally recognized third party that requires periodic follow-up inspections and a has a listing directory available to the public. Third party listing shall be by [ICC-ES Product Listing] [UL Product Listing] [FM Approvals] [an evaluation service member of ICC-ES] [an agency acceptable to authorities having jurisdiction].

        - Calculations (including combining shear and tensile loads) to support seismic-restraint designs must be signed and sealed by a qualified professional engineer.

        - Consequential Damage: Provide additional seismic restraints for suspended plumbing components or anchorage of floor-, roof-, or wall-mounted plumbing components so that failure of a non-essential or essential plumbing component will not cause the failure of any other essential architectural, mechanical, or electrical building component.

        - Fire/Smoke Resistance: Seismic[ and wind load] restraint devices that are not constructed of ferrous metals shall comply with IMC 602, maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested by an NRTL in accordance with ASTM E84 or UL 723, and be so labeled.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

See the Evaluations for more detailed information about controlling vibration, additional information on products described in this Section, illustrations, selection guides, and supplements to Equipment Schedules.

Coordinate specifications for products in this Section with Project structural engineer and with Drawings.

      - PERFORMANCE REQUIREMENTS

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

        - Delegated Design: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design seismic[ and wind-load] control system.

Retain "Seismic Performance" Subparagraph below for projects requiring seismic design. Delete subparagraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

          - Seismic Performance: Equipment must be designed and secured to withstand the effects of earthquake motions determined in accordance with [NFPA 13-16 for 2018 IBC] [NFPA 13-19 for most recent edition] <Insert NFPA 13 Edition> and ASCE/SEI 7-16.

Retain "Wind-Load Performance" Subparagraph below if wind-load protection is required.

          - Wind-Load Performance: Equipment must be designed and secured to withstand the effects of high wind events determined in accordance with ASCE/SEI 7-16 .

Retain "Seismic Design Calculations" Paragraph and applicable calculation factors subparagraph below if seismic design services have been delegated to Contractor.

        - Seismic Design Calculations:

NFPA 13 and ASCE/SEI 7 are generally applicable in most locations, but it is fire-suppression system engineer's responsibility to determine the applicable building codes and editions thereof, and applicable seismic design standards that apply to Project. Data and information required for seismic calculations in NFPA 13 and ASCE/SEI 7 are listed below.

If a calculation method other than that prescribed in any edition of ASCE/SEI 7 is applicable to Project, fire-suppression system engineer must revise the Section Text to provide alternative appropriate calculation parameters and instructions for delegated designer in lieu of those given below.

          - Perform calculations to obtain force information necessary to properly select seismic-restraint devices, fasteners, and anchorage. Perform calculations using methods acceptable to applicable code authorities and as presented in [NFPA 13-16 for 2018 IBC] [NFPA 13-19 for most recent edition] <Insert NFPA 13 Edition> and [ASCE/SEI 7-16 for 2018 IBC] <Insert ASCE/SEI 7 edition or other seismic calculation method required by authorities having jurisdiction>. Where "ASCE/SEI 7" is used throughout this Section, it is to be understood that the edition referred to in this subparagraph is the edition intended as reference throughout the Section Text.

            - Data indicated below to be determined by Delegated Design Contractor must be obtained by Contractor and must be included in individual component submittal packages.

Retain first subparagraph below if wind-load design is delegated to Contractor.

            - Coordinate seismic design calculations with wind-load calculations for equipment mounted outdoors. Comply with requirements in other Sections in addition to those in this Section for equipment mounted outdoors.

Data values identified below as applying to all components on Project are to be inserted by fire-suppression system engineer in these Specifications where indicated in the following list. Data values that are specific to an individual generic component and are indicated to be scheduled should be included by fire-suppression system engineer in Fire-Suppression System Vibration Isolation, and Seismic Load Restraints Schedule or the individual component schedules on Drawings. Data values that are specific to an individual piece of equipment as provided by Contractor and are indicated to be obtained by Contractor must be included in individual component submittal packages.

The term "Building Risk Category" is used in ASCE/SEI 7-16. Fire-suppression system engineer must obtain the value from Project structural engineer and retain first subparagraph below.

            - Building Risk Category: [I] [II] [III] [IV].

Fire-suppression system engineer must obtain "Building Site Classification" value from Project structural engineer and retain first subparagraph below.

            - Building Site Classification: [A] [B] [C] [D] [E] [F].

Retain "Calculation Factors, ASCE/SEI 7-16, Ch. 13 - Seismic Design Requirements for Nonstructural Components" Subparagraph below if ASCE/SEI 7-16 applies to this Project.

          - Calculation Factors, ASCE/SEI 7-16, Ch. 13 - Seismic Design Requirements for Nonstructural Components: All section, paragraph, equation, and table numbers refer to ASCE/SEI 7-16 unless otherwise noted.

            - Horizontal Seismic Design Force Fp: Value is to be calculated by Delegated Design Contractor using ASCE/SEI 7-16 Equation 13.3-1. Factors below must be obtained for this calculation.

"Spectral Acceleration" value applies to all components on Project. Value is to be obtained by fire-suppression system engineer from Project structural engineer based on ASCE/SEI 7-16 Section 11.4.5.

              - SDS = Spectral Acceleration: <Insert value>. Value applies to all components on Project.

"Component Amplification Factor" for each component is selected by fire-suppression system engineer as explained in ASCE/SEI 7-16 Section 13.6.1. List on Drawing Schedule for each component.

              - ap = Component Amplification Factor: See Drawing Schedule for each component.

"Component Importance Factor" is assigned by fire-suppression system engineer as explained in ASCE/SEI 7-16 Section 13.1.3. List on Drawing Schedule for each component.

              - Ip = Component Importance Factor: See Drawing Schedule for each component.

              - Wp = Component Operating Weight: For each component. Obtain by Delegated Design Contractor from each component submittal.

"Component Response Modification Factor" is selected by fire-suppression system engineer from ASCE/SEI 7-16, Table 13.6-1. List on Drawing Schedule for each component.

              - Rp = Component Response Modification Factor: See Drawing Schedule for each component.

              - z = Height in Structure of Point of Attachment of Component for Base: Determine from Project Drawings for each component by Delegated Design Contractor. For items at or below the base, "z" shall be taken as zero.

              - h = Average Roof Height of Structure for Base: Determine from Project Drawings by Delegated Design Contractor.

            - Vertical Seismic Design Force: Calculated by Delegated Design Contractor using method explained in ASCE/SEI 7-16, Paragraph 13.3.1.2.

            - Seismic Relative Displacement: Comply with [NFPA 13-16 for 2018 IBC] [NFPA 13-19 for most recent edition] <Insert NFPA 13 Edition> requirements for flexibility and clearance or Dpl shall be Calculated by Delegated Design Contractor using methods explained in ASCE/SEI 7-16, Paragraph 13.3.2. Factors below must be obtained for this calculation:

              - Dp = Relative Seismic Displacement that Each Component Must Be Designed to Accommodate: Calculated by Delegated Design Contractor in accordance with ASCE/SEI 7-16, Paragraph 13.3.2.

"Structure Importance Factor" is assigned by fire-suppression system engineer from Project structural engineer and ASCE/SEI 7-16 Section 11.5.1.

              - Ie = Structure Importance Factor: <Insert value>. Value applies to all components on Project.

"Deflection at building level x of Structure A" value is determined for each component in building in accordance with ASCE/SEI 7-16, Equation 12.8-15 and depends upon location of component in the building. Value is obtained by fire-suppression system engineer from Project structural engineer.

              - δxA = Deflection at Building Level x of Structure A: See Drawing Schedule for each component.

"Deflection at building level y of Structure A" value is determined for each component in building in accordance with ASCE/SEI 7-16, Equation 12.8-15 and depends upon location of component in the building. Value is obtained by fire-suppression system engineer from Project structural engineer.

              - δyA = Deflection at Building Level y of Structure A: See Drawing Schedule for each component.

"Deflection at building level y of Structure B" value is determined for each component in building in accordance with ASCE/SEI 7-16, Equation 12.8-15 and depends upon location of component in the building. Value is obtained by fire-suppression system engineer from Project structural engineer.

              - δyB = Deflection at Building Level y of Structure B: See Drawing Schedule for each component.

              - hx = Height of Level x to which Upper Connection Point Is Attached: Determine for each component by Delegated Design Contractor from Project Drawings and manufacturer's data.

              - hy = Height of Level y to which Upper Connection Point Is Attached: Determine for each component by Delegated Design Contractor from Project Drawings and manufacturer's data.

"Allowable story drift for Structure A" value is determined in accordance with ASCE/SEI 7-16, Equation 12.12-1 and depends upon location of component in the building. Value is obtained by fire-suppression system engineer from Project structural engineer.

              - ΔaA = Allowable Story Drift for Structure A: See Drawing Schedules for each component.

"Allowable story drift for Structure B" value is determined in accordance with ASCE/SEI 7-16, Equation 12.12-1 and depends upon location of component in the building. Value is obtained by fire-suppression system engineer from Project structural engineer.

              - ΔaB = Allowable Story Drift for Structure B: See Drawing Schedules for each component.

"Story Height" used in the definition of the "allowable drift" value is determined in accordance with ASCE/SEI 7-16, Table 12.12-1 and depends upon location of component in the building. Value is obtained by fire-suppression system engineer from Project structural engineer.

              - hsx = Story Height Used in the Definition of the Allowable Drift Δa: See Drawings Schedules for each component.

            - Component Fundamental Period Tp: Calculated by Delegated Design Contractor using methods explained in ASCE/SEI 7-16, Paragraph 13.3.3. Factors below must be obtained for this calculation:

              - Wp = Component Operating Weight: Determined by contractor from Project Drawings and manufacturer's data.

              - g = Gravitational Acceleration: [32.17 fps2 (9.81 m/s2)] <Insert option>.

              - Kp = Combined Stiffness of Component, Supports, and Attachments: Determined by delegated design seismic engineer. <Insert value>.

        - Allowable Stresses on Pipe and Tube:

          - Unless piping or tubing is designed with flexible connections to avoid component failure at component connections, or components such as valves, strainers, traps, pumps, air separators, and tanks are mounted inline and laterally braced as part of pipe or tube, or components are braced independently, because of their weight, with flexible connections to components; the pipe or tube, other than ASME pressure piping, shall be designed based on the following allowable stresses.

            - 90 percent of the minimum yield strength for ductile piping, such as steel, aluminum, or copper, with welded or brazed connections.

            - 70 percent of the minimum yield strength for ductile piping, such as steel, aluminum, or copper, with threaded, bonded, compression coupling or grooved coupling connections.

            - 10 percent of the minimum yield strength for nonductile piping, such as cast iron or ceramics, with compression coupling or grooved coupling connections.

            - 8 percent of the minimum yield strength for nonductile piping with threaded connections.

          - NFPA 13 Piping Systems: Fire-suppression piping systems, including their supports, designed and constructed in accordance with NFPA 13 requirements for Maximum Fpw, shall be deemed to meet the seismic requirements of this Section.

        - Exceptions to the seismic protection requirements of this Section for fire-suppression piping components based on component size or method of attachment: NFPA 13 exemptions to requirements for flexibility, clearance, and seismic restraint shall be deemed to meet the seismic requirements of this Section.

          - NFPA 13 makes a distinction between the terms "braces," which are seismic restraints, and "restraints," which are also seismic restraints. The difference is that NFPA 13 "restraints" are used on 2-inch and smaller branch line piping and do not require supporting calculations. The term "seismic restraint" in this Section refers to all forms of seismic restraints.

Retain "Wind-Load Design Calculations" Paragraph and applicable calculation factors subparagraph if wind-load reinforcement design services have been delegated to Contractor.

        - Wind-Load Design Calculations:

ASCE/SEI 7 and NFPA 13 are generally applicable in most locations, but it is fire-suppression system engineer's responsibility to determine the applicable building codes and editions thereof, and applicable wind-load design standards that apply to this Project.

If a calculation method other than that prescribed in ASCE/SEI 7 is to be used, fire-suppression system engineer must revise the Section Text to provide alternative appropriate calculation parameters and instruction for delegated designer in lieu of those given below.

          - Perform calculations to obtain force information necessary to properly select wind-load-restraint devices, fasteners, and anchorage. Perform calculations using methods acceptable to applicable code authorities and as presented in [ASCE/SEI 7-16 for 2018 IBC] <Insert ASCE/SEI 7 edition or other wind-load calculation method required by authorities having jurisdiction>. Where "ASCE/SEI 7" is used throughout this Section, it is to be understood that the edition referred to in this subparagraph is intended as referenced throughout the Section Text unless otherwise noted.

            - Factors indicated below that are specific to individual pieces of equipment must be obtained by Contractor and must be included in individual component submittal packages.

            - Coordinate design wind-load calculations with seismic load calculations for equipment requiring both seismic and wind-load reinforcement. Comply with requirements in other Sections in addition to those in this Section for equipment mounted outdoors.

Data values identified below as applying to all components on Project are to be inserted by fire-suppression system engineer in these Specifications where indicated in the following list. Data values that are specific to an individual generic component and are indicated to be scheduled should be included by fire-suppression system engineer in Fire-Suppression System Vibration Isolation, Seismic, and Wind-Load-Restraint Schedule or the individual component schedules on Drawings. Data values that are specific to an individual piece of equipment as provided by Contractor and are indicated to be obtained by Contractor must be included in individual component submittal packages.

          - Design wind pressure "p" for external sidewall-mounted equipment is to be calculated by Delegated Design Contractor using methods in ASCE/SEI 7-16, Ch. 30. Perform calculations in accordance with one of the following, as appropriate:

            - PART 1: Low-Rise Buildings.

            - PART 2: Low-Rise Buildings (Simplified).

            - PART 3: Buildings with "h" less than 60 ft. (18.3 m).

            - PART 4: Buildings with "h" greater than 60 ft. (18.3 m) and less than 160 ft. (48.8 m).

            - PART 5: Open Buildings.

          - Design wind pressure "p" for rooftop equipment is to be calculated by Delegated Design Contractor using methods in ASCE/SEI 7-16, Ch 30, PART 6: Building Appurtenances and Rooftop Structures and Equipment.

"Risk category" value is determined by fire-suppression system engineer from Project structural engineer or ASCE/SEI 7-16, Table 1.5-1.

              - Risk Category: [I] [II] [III] [IV] [V].

"Mean Roof Height" is determined by fire-suppression system engineer from Project Drawings.

              - h = Mean Roof Height: <Insert value>.

"Basic Wind Speed" value is obtained by fire-suppression system engineer from Wind Hazard map in ASCE/SEI 7-16 Section 26.5 or other source approved by authorities having jurisdiction.

              - V = Basic Wind Speed: <Insert value>.

"Wind directionality factor" value is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.6 and Table 26.6-1 or other source approved by authorities having jurisdiction.

              - Kd = Wind Directionality Factor: <Insert factor>.

"Exposure category" value is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.7 or other source approved by authorities having jurisdiction.

              - Exposure Category: [B] [C] [D].

"Topographic factor" value is obtained by fire-suppression system engineer from ASCE/SEI 7-16, Section 26.8 and Table 26.8-1 or other source approved by authorities having jurisdiction.

              - Kzt = Topographic Factor: <Insert factor>.

"Ground elevation factor" value is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.8 and Table 26.8-1 or other source approved by authorities having jurisdiction.

              - Ke = Ground Elevation Factor: <Insert factor>.

"Velocity pressure exposure coefficient" value at height z and height h is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.10.1 or other source approved by authorities having jurisdiction.

              - Kz = Velocity Pressure Exposure Coefficient (Evaluated at Height z): <Insert coefficient>.

              - Kh = Velocity Pressure Exposure Coefficient (Evaluated at Height h): <Insert coefficient>.

              - qz = Velocity Pressure: Value calculated by delegated wind-load design Contractor using methods detailed in ASCE/SEI 7-16 Section 26.10.1 or other source approved by authorities having jurisdiction.

              - qh =	 Velocity Pressure: Value calculated by delegated wind-load design Contractor using methods detailed in ASCE/SEI 7-16 Section 26.10.1 or other source approved by authorities having jurisdiction.

"Gust-effect factor" is obtained by fire-suppression system engineer form ASCE/SEI 7-16 Section 26.11 or other source approved by authorities having jurisdiction.

              - G = Gust-Effect Factor: [0.85] <Insert factor>.

"Enclosure classification" is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.12 or other source approved by authorities having jurisdiction.

              - Enclosure Classification: <Insert classification>.

"Internal pressure coefficient" is obtained by fire-suppression system engineer from ASCE/SEI 7-16, Table 26.13-1 or other source approved by authorities having jurisdiction.

              - GCpi = Internal Pressure Coefficient: <Insert coefficient>.

        - Consequential Damage: Provide additional seismic and wind-load restraints for suspended fire-suppression system components or anchorage of floor-, roof-, or wall-mounted fire-suppression system components as indicated in ASCE/SEI 7-16 so that failure of a non-essential or essential fire-suppression system component will not cause the failure of any other essential architectural, mechanical, or electrical building component.

        - Fire/Smoke Resistance: Seismic-[ and wind-load-]restraint devices that are not constructed of ferrous metals must have a maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested by an NRTL in accordance with ASTM E84 or UL 723, and be so labeled.

        - Seismic-Restraint Loading:

          - Load ratings, features, and applications shall be as defined in ICC-ES Product Listings, UL Product Listings, ICC-ES Evaluation Reports, OSHPD, or an agency acceptable to authorities having jurisdiction.

            - Load Ratings for seismic restraint components shall include a minimum safety factor of 2.2.

          - Standard supports, such as ASME B31, NFPA 13, MSS SP-58, or proprietary supports, shall be designed by load rating or for the calculated seismic forces.

          - Component supports, such as structural members, braces, frames, skirts, legs, saddles, pedestals, cables, guys, stays, snubbers, tethers, and elements forged or cast into a mechanical component, shall be designed for the seismic forces and displacements, including displacement between piping supports.

          - The means by which supports are attached to the component, except where cast or forged into the component, including the region of support engagement to the component wall where Ip equals 1.5, shall be designed to accommodate the seismic forces and displacements and to maintain support engagement.

          - The materials comprising supports and the means of attachment to the component, including weak-axis bending of cold-formed steel supports, shall be constructed of materials suitable for the application, including the effects of service conditions and shall be in conformance with a nationally recognized standard.

          - Reinforcement shall be provided at bolted connections through sheet metal equipment housings as required to transfer seismic loads from the equipment to the structure. The design force shall be taken as 2Fp, if the nominal clearance (air gap) between the equipment support frame and restraint is greater than 0.25 in. (6 mm).

Retain "Wind Restraint Loading" Paragraph below for outdoor equipment.

        - Wind Restraint Loading:

Obtain values for items in subparagraphs below from Project structural engineer or from ASCE/SEI 7.

          - Basic Wind Speed: As defined by wind speed maps in ASCE/SEI 7-16. Wind Hazard Map <Insert value> mi/h (m∕s) at 33 ft. (10 m) above ground for Exposure Category C. <Insert value>.

          - Minimum 10 lb/sq. ft. (48.8 kg/sq. m) multiplied by maximum area of plumbing component projected on vertical plane normal to wind direction, and 45 degrees either side of normal.

          - Perform wind-loading calculations in accordance with ASCE/SEI 7.

      - ELASTOMERIC ISOLATION PADS

Copy "Elastomeric Isolation Pads" Paragraph below and re-edit for each product.

Configuration and materials of elastomeric isolation pads depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation pad on same Project. Insert Drawing designation for each elastomeric isolation pad type required. Use these designations on Drawings to identify each product.

For information on CADDY, a brand of nVent Rubber Pads, refer to http://www.vimco.biz/filecabinet/vimco/Literature/P-2201.pdf

        - Elastomeric Isolation Pads, CSBRP: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY; a brand of nVent; Elastomeric Isolation Pads or a comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Fabrication: Single or multiple layers of sufficient durometer stiffness for uniform loading over pad area.

          - Size: Factory or field cut to match requirements of supported equipment.

          - Pad Material: Oil and water resistant with elastomeric properties. Neoprene rubber, silicone rubber, or other elastomeric material.

          - Surface Pattern: Smooth, ribbed, or waffle pattern.

Retain first subparagraph below if pad is infused with synthetic fibers.

          - Infused nonwoven cotton or synthetic fibers.

Retain first subparagraph below if galvanized-steel baseplates are adhered to isolation pad to facilitate load distribution.

          - Load-bearing metal plates adhered to pads.

Retain "Sandwich-Core Material" Subparagraph below if pad has a sandwich-core material.

Copy below and re-edit for each sandwich-core material. Core materials may not be elastomeric. See "Elastomeric Isolation Pads" Article in the Evaluations for more information.

          - Sandwich-Core Material: [Resilient] [and] [elastomeric] <Insert compound>.

Retain "Surface Pattern" Subparagraph below if the sandwich-core material has a surface pattern.

            - Surface Pattern: Smooth, ribbed, or waffle pattern.

Retain subparagraph below if pad is infused with synthetic fibers.

            - Infused nonwoven cotton or synthetic fibers.

      - ELASTOMERIC ISOLATION MOUNTS

Copy "Double-Deflection, Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

Configuration and materials of elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation mount on same Project. Insert drawing designation. Use these designations on Drawings to identify each product.

For information on CADDY, a brand of nVent Rubber Mounts, refer to http://www.vimco.biz/filecabinet/vimco/Literature/S-2225-01.pdf.

        - Double-Deflection, Elastomeric Isolation Mounts: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY; a brand of nVent; Elastomeric Isolation Mounts or a comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Mounting Plates:

            - Top Plate: Encapsulated steel load transfer top plates, factory drilled and threaded[ with threaded studs or bolts].

Retain "Baseplate" Subparagraph below if the elastomeric mount being specified has a baseplate.

            - Baseplate: Encapsulated steel bottom plates with holes provided for anchoring to support structure.

          - Elastomeric Material: Molded, oil- and water-resistant neoprene rubber, silicone rubber, or other elastomeric material.

      - RESTRAINED ELASTOMERIC ISOLATION MOUNTS

Copy "Restrained Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

Configuration and materials of restrained elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of restrained elastomeric isolation mount on same Project. Insert drawing designation. Use these designations on Drawings to identify each product.

For information on CADDY, a brand of nVent Rubber Mounts, refer to http://www.vimco.biz/filecabinet/vimco/Literature/S-3100-61.pdf.

        - Restrained Elastomeric Isolation Mounts: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY; a brand of nVent; Restrained Elastomeric Isolation Mounts or a comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Description: All-directional isolator with seismic restraints containing two separate and opposing elastomeric elements that prevent central threaded element and attachment hardware from contacting the housing during normal operation.

            - Housing: Cast-ductile iron or welded steel.

            - Elastomeric Material: Molded, oil-resistant rubber, neoprene, or other elastomeric material.

      - ELASTOMERIC HANGERS

Copy "Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods" Paragraph below and re-edit for each product.

Configuration and materials of elastomeric hangers depend on the equipment being supported. It is possible to have more than one type of elastomeric hanger on same Project. Insert drawing designation. Use these designations on Drawings to identify each product.

        - Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY; a brand of nVent; Elastomeric Hangers or a comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Frame: Steel, fabricated with a connection for an upper threaded hanger rod and an opening on the underside to allow for a maximum of 30 degrees of angular lower hanger-rod misalignment without binding or reducing isolation efficiency.

          - Damping Element: Molded, oil-resistant rubber, neoprene, or other elastomeric material with a projecting bushing for the underside opening preventing steel-to-steel contact.

      - SNUBBERS

For information on CADDY, a brand of nVent Seismic Snubbers, refer to http://www.vimco.biz/filecabinet/vimco/Literature/S-3100-51.pdf.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY; a brand of nVent; Snubbers or a comparable product by one of the following:

          - Vibration Management Corp.

          - Vibration Mountings & Controls, Inc.

          - <Insert manufacturer's name>.

        - Description: Factory fabricated using welded structural-steel shapes and plates, anchor bolts, and replaceable resilient isolation washers and bushings.

          - Post-Installed Concrete Anchor Bolts: Secure to concrete surface with post-installed concrete anchors. Anchors to be seismically prequalified in accordance with ACI 355.2 testing and designated in accordance with ACI 318-14 Ch. 17.

          - Preset Concrete Inserts: Seismically prequalified in accordance with ICC-ES AC446 testing.

          - Anchors in Masonry: Design in accordance with TMS 402.

          - Resilient Isolation Washers and Bushings: Oil- and water-resistant neoprene.

          - Resilient Cushion: Maximum 1/4-inch (6-mm) air gap, and minimum 1/4 inch (6 mm) thick.

      - SEISMIC RESTRAINTS - RIGID TYPE

For information on CADDY, a brand of nVent Rigid Seismic Bracing, refer to https://www.erico.com/category.asp?category=R152

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY; a brand of nVent; CADDY Structure Attachments, Sway Braces, and Lateral Telescoping Brace Assemblies for Rigid Seismic Bracing or a comparable product by one of the following:

          - B-line, an Eaton business.

          - Unistrut; Part of Atkore International.

          - <Insert manufacturer's name>.

        - Description: Shop- or field-fabricated bracing assembly made of AISI S110-07-S1 slotted steel channels, ANSI/ASTM A53/A53M steel pipe as per NFPA 13, or other rigid steel brace member. Includes accessories for attachment to braced component at one end and to building structure at the other end and other matching components and with corrosion-resistant coating; rated in tension, compression, and torsion forces.

      - SEISMIC RESTRAINTS - CABLE TYPE

For information on CADDY, a brand of nVent Seismic Wire Rope/Cable™ Bracing, refer to https://www.erico.com/category.asp?category=R146.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY; a brand of nVent; Size 12 RED, Size 18 WHITE, Size 36 BLUE, or Size 48 YELLOW Seismic Wire Rope/Cable Bracing or a comparable product by one of the following:

          - Loos & Co.

          - Vibration Mountings & Controls, Inc.

          - <Insert manufacturer's name>.

        - Seismic-Restraint Cables: [ASTM A1023/A12023M galvanized or ASTM A603 galvanized-steel] [ASTM A492 stainless steel] cables. End connections made of steel assemblies with thimbles, brackets, swivel, and bolts designed for seismic restraining cable service; with fittings attached by means of poured socket, swaged socket or mechanical (Flemish eye) loop.

        - Restraint cable assembly with cable fittings must comply with ASCE/SEI 19. All cable fittings and complete cable assembly must maintain the minimum cable breaking force. U-shaped cable clips and wedge-type end fittings do not comply and are unacceptable.

      - SEISMIC RESTRAINT ACCESSORIES

For information on CADDY, a brand of nVent Seismic Wire Rope/Cable™ Bracing Accessories, refer to https://www.erico.com/category.asp?category=R146.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY; a brand of nVent; Size 12 RED, Size 18 WHITE, Size 36 BLUE, or Size 48 YELLOW Seismic Wire Rope/Cable Spools and Oval Sleeves, URC Universal Restraint Clips, NPC No-Pry Clips, Quick Clip and RS-1 Rod Stiffener Clips, and Structure Attachment and Sway Brace fittings for 1 to 2 inch brace members or a comparable product by one of the following:

          - Vibration Eliminator Co., Inc.

          - Vibration & Seismic Technologies, LLC.

          - <Insert manufacturer's name>.

Retain "Hanger-Rod Stiffener" Paragraph below for strengthening resistance of hanger rods against seismic and wind forces that may cause buckling of rods; delete if detailed on Drawings. Use with either rigid- or cable-type bracing assemblies when required to counter seismic and wind forces. Detail fabrication and indicate locations on Drawings.

For information on CADDY, a brand of nVent Seismic Wire Rope/Cable™ Bracing Accessories, refer to https://www.erico.com/category.asp?category=R146.

        - Hanger-Rod Stiffener: Steel tube, steel channel-type strut, or steel angle rod stiffener member clamped to hanger rod with rod stiffener clips. Non-metallic stiffeners are unacceptable.

        - Hinged and Swivel Brace Attachments: Multifunctional steel connectors for attaching hangers to [seismic restraints - rigid-type] [and] [seismic restraints - cable-type].

        - Bushings for Floor-Mounted Equipment Anchor Bolts: Neoprene bushings designed for rigid equipment mountings, and matched to type and size of anchor bolts and studs.

        - Resilient Isolation Washers and Bushings: One-piece, molded, oil- and water-resistant neoprene, with a flat washer face.

      - POST-INSTALLED CONCRETE ANCHORS IN CONCRETE AND MASONRY

For information on CADDY, a brand of nVent Post-Installed Concrete Anchors, refer to https://www.erico.com/category.asp?category=R1250

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY; a brand of nVent; CADDY Wedge Expansion Anchors, Screw Anchors, or comparable product by one of the following:

          - Powers Fasteners.

          - Simpson Strong-Tie Co., Inc.

          - <Insert manufacturer's name>.

        - Post-Installed expansion and undercut anchors in concrete and masonry to be seismically pre-qualified in accordance with ACI 355.2 testing.

        - Post-installed adhesive anchors in concrete and masonry to be seismically pre-qualified in accordance with ACI 355.4 testing.

        - Post-installed anchors in concrete to be designated in accordance with ACI 318-14 Chapter 17.

        - Post-installed anchors in masonry to be designed in accordance with TMS 402.

      - CONCRETE INSERTS

For information on CADDY, a brand of nVent Rod Lock Concrete Inserts, refer to https://www.erico.com/category.asp?category=R2853.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY, Rod Lock Metal Deck and Plywood Form Inserts or comparable product by one of the following:

          - Powers Fasteners.

          - Simpson Strong-Tie Co., Inc.

          - <Insert manufacturer's name>.

        - Preset Concrete Inserts: To be seismically pre-qualified in accordance with ICC-ES AC446.

        - Provide post-installed concrete anchors that have been prequalified for use in seismic applications. Post-installed concrete anchors must comply with all requirements of ASCE/SEI 7-16 Ch. 13.

          - Prequalify post-installed anchors in concrete in accordance with ACI 355.2 or other approved qualification testing procedures.

          - Prequalify post-installed anchors in masonry in accordance with approved qualification procedures.

- EXECUTION

      - EXAMINATION

        - Examine areas and equipment to receive vibration isolation[, wind control,] and seismic control devices for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in of reinforcement and cast-in-place anchors to verify actual locations before installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - APPLICATIONS

        - Multiple Pipe Supports: Secure pipes to trapeze member with clamps approved for application by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

Indicate on Drawings, in schedules, or a combination of both, locations where hanger rods for individual pipes and hanger rods for trapeze hangers require hanger-rod stiffeners.

        - Hanger-Rod Stiffeners: Install where indicated or scheduled on Drawings to receive them and where required to prevent buckling of hanger rods due to seismic forces.

        - Strength of Support and Seismic-Restraint Assemblies: Where not indicated, select sizes of components so strength is adequate to carry calculated static[, wind load,] and seismic loads within specified loading limits.

      - INSTALLATION OF VIBRATION CONTROL[, WIND-LOAD-RESTRAINT,] AND SEISMIC-RESTRAINT DEVICES

        - Provide vibration-control devices for systems and equipment where indicated in Equipment Schedules or Fire-Suppression Vibration Isolation, Seismic, and Wind-Load-Restraint Schedule, where indicated on Drawings, or where the Specifications indicate they are to be installed on specific equipment and systems.

        - Provide seismic-restraint [and wind-load-restraint ]devices for systems and equipment where indicated in Equipment Schedules or Vibration Isolation, Seismic, and Wind-Load-Restraint Schedules, where indicated on Drawings, where the Specifications indicate they are to be installed on specific equipment and systems, and where required by applicable codes.

        - Coordinate location of embedded connection hardware with supported equipment attachment and mounting points and with requirements for concrete reinforcement and formwork specified in Section 033000 "Cast-in-Place Concrete."

        - Installation of vibration isolators[, wind-load restraints,] and seismic restraints must not cause any stresses, misalignment, or change of position of equipment or piping.

        - Comply with installation requirements of NFPA 13 for installation of all seismic-restraint devices.

        - Comply with requirements in Section 077200 "Roof Accessories" for installation of equipment supports and roof penetrations.

        - Equipment Restraints:

Indicate type and quantity of snubbers, wind-load restraint, and seismic-restraint devices described in three subparagraphs below, on Drawings, or in Fire-Suppression Vibration Isolation, Seismic, and Wind-Load-Restraint Schedule on Drawings.

          - Install snubbers on fire-suppression equipment mounted on vibration isolators. Locate snubbers as close as possible to vibration isolators and bolt to equipment base and supporting structure.

          - Install resilient bolt isolation washers on equipment anchor bolts where clearance between anchor and adjacent surface exceeds 0.125 inch (3.2 mm).

          - Install seismic-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] that provides required submittals for component.

        - Piping Restraints:

          - Comply with all requirements in NFPA 13.

          - Design piping sway bracing in accordance with NFPA 13.

            - Maximum spacing of all sway bracing to be no greater than indicated in NFPA 13.

            - Design loading of all sway bracing not to exceed values indicated in NFPA 13.

        - Install seismic-[ and wind-load-]restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] that provides required submittals for component.

        - Install bushing assemblies for anchor bolts for floor-mounted equipment, arranged to provide resilient media between anchor bolt and mounting hole in concrete base.

        - Install bushing assemblies for mounting bolts for wall-mounted equipment, arranged to provide resilient media where equipment or equipment-mounting channels are attached to wall.

        - Attachment to Structure: If specific attachment is not indicated, anchor bracing to structure at flanges of beams, at upper truss chords of bar joists, or at concrete members.

        - Post-Installed Concrete Anchors:

          - Identify position of reinforcing steel and other embedded items prior to drilling holes for anchors. Do not damage existing reinforcing or embedded items during coring or drilling. Notify the structural engineer if reinforcing steel or other embedded items are encountered during drilling. Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

          - Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

          - Wedge-Type Anchor Bolts: Protect threads from damage during anchor installation. Heavy-duty sleeve anchors shall be installed with sleeve fully engaged in the structural element to which anchor is to be fastened.

          - Adhesive-Type Anchor Bolts: Clean holes to remove loose material and drilling dust prior to installation of adhesive. Place adhesive in holes proceeding from the bottom of the hole and progressing toward the surface in such a manner as to avoid introduction of air pockets in the adhesive.

          - Set anchors to manufacturer's recommended torque, using a torque wrench.

          - Install zinc-coated steel anchors for interior and stainless steel anchors for exterior applications.

      - ACCOMMODATION OF DIFFERENTIAL SEISMIC MOTION

Coordinate this article with Drawings.

        - Install flexible connections in piping where they cross structural seismic joints and other points where differential movement may occur, where adjacent sections or branches are supported by different structural elements, and where the connections terminate with connection to equipment that is anchored to a different structural element from the one supporting the connections as they approach equipment. Comply with requirements in Section 211200 "Fire-Suppression Standpipes," Section 211313 "Wet-Pipe Sprinkler Systems," and Section 211316 "Dry-Pipe Sprinkler Systems" for piping flexible connections.

      - ADJUSTING

        - Adjust isolators after system is at operating weight.

        - Adjust limit stops on restrained-spring isolators to mount equipment at normal operating height. After equipment installation is complete, adjust limit stops so they are out of contact during normal operation.

      - FIELD QUALITY CONTROL

Retain first option in "Testing Agency" Paragraph below if Owner will hire an independent testing agency.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

        - Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

        - Tests and Inspections:

          - Provide evidence of recent calibration of test equipment by a testing agency acceptable to authorities having jurisdiction.

          - Schedule test with Owner, through Architect, before connecting anchorage device to restrained component (unless postconnection testing has been approved), and with at least seven days' advance notice.

          - Obtain Architect's approval before transmitting test loads to structure. Provide temporary load-spreading members.

          - Test at no fewer than [four] <Insert number> of each type and size of installed anchors and fasteners selected by Architect.

          - Test to 90 percent of rated proof load of device.

          - Measure isolator restraint clearance.

          - Measure isolator deflection.

          - Verify snubber minimum clearances.

        - Remove and replace malfunctioning units and retest as specified above.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Units will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

END OF SECTION 201548