Copyright 2018 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to CADDY, a brand of nVent ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact nVent, 7433 31700 Solon Road, Solon, OH 44139; Phone: (800) 753-9221 | (440) 248-0100; Fax: (440) 848-8405; Website: www.nvent.com; Email: Daniel.Duggan@nVent.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 230548 - VIBRATION AND SEISMIC CONTROLS FOR HVAC

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Use this Section if Project is in a seismic area. Use Section 230548.13 "Vibration Controls for HVAC" for Projects not in a seismic area.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Elastomeric isolation pads.

          - Elastomeric isolation mounts.

          - Restrained elastomeric isolation mounts.

          - Open-spring isolators.

          - Housed-spring isolators.

          - Restrained-spring isolators.

          - Housed-restrained-spring isolators.

          - Pipe-riser resilient supports.

          - Resilient pipe guides.

          - Air-spring isolators.

          - Restrained-air-spring isolators.

          - Elastomeric hangers.

          - Spring hangers.

          - Snubbers.

          - Seismic restraints – rigid type.

          - Seismic restraints – cable type.

          - Seismic-restraint accessories.

          - Post-installed concrete anchors in concrete and masonry.

          - Concrete inserts.

          - Vibration isolation equipment bases.

          - Restrained isolation roof-curb rails.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 210548 "Vibration and Seismic Controls for Fire Suppression" for devices for fire-suppression equipment and systems.

          - Section 220548 "Vibration and Seismic Controls for Plumbing" for devices for plumbing equipment and systems.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - FM: Factory Mutual.

        - ASCE: American Society of Civil Engineers.

        - Designated Seismic System: An HVAC component that requires design in accordance with ASCE 7, Chapter 13 and for which the component Importance Factor is greater than 1.00.

        - IBC: International Building Code.

        - ICC-ES: International Code Council-Evaluation Service.

        - IMC: International Mechanical Code.

        - MFMA: Metal Framing Manufacturers Association.

        - NRTL: Nationally recognized testing laboratory.

The OPA program has been discontinued and replaced by OPM, but existing OPA numbers can be used for projects based on the code cycle under which OPAs were approved.

        - OPA: OSHPD Preapproval of anchorage number, Office of Statewide Health Planning & Development (for the State of California owned and regulated medical facilities).

        - OPM: Manufacturer’s Preapproval Certification Number (for the State of California owned and regulated medical facilities).

        - OSHPD: Office of Statewide Health Planning and Development (for the State of California owned and regulated medical facilities).

        - UL: Underwriters Laboratories.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include rated load, rated deflection, and overload capacity for each vibration isolation device.

          - Include load rating for each seismic restraint fitting or assembly and prying factor for each seismic restraint structure attachment fitting.

          - Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of vibration isolation device and seismic-restraint component required.

See the Evaluations for a discussion on seismic-restraint capacities and rating services. Retain all that apply.

            - Tabulate types and sizes of seismic restraints and accessories, complete with listing markings or report numbers and load rating in tension and compression as evaluated by [ICC-ES Product Listing] [UL Product Listing] [FM Approval] [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

            - Annotate to indicate application of each product submitted and compliance with requirements.

          - Interlocking Snubbers: Include ratings for horizontal, vertical, and combined loads.

        - Shop Drawings:

          - Detail fabrication and assembly of equipment bases. Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting.

          - Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting.

Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Contractor.

        - Delegated-Design Submittal: For each vibration isolation[, and] seismic-restraint[, and wind force] device that is required by this Section or is shown on the contract documents, submit the following:

          - Design Calculations: Calculate static or dynamic loading as required by ASCE 7 due to equipment weight, operation, and seismic[ and wind] forces required for selection of vibration isolators and seismic[ and wind] restraints, and for design of vibration isolation bases.

            - Coordinate design calculations with wind load calculations required for equipment mounted outdoors. Comply with requirements in other Sections for equipment mounted outdoors.

            - All calculations are to be performed using methods defined in [ASCE 7-05 for 2009 IBC] [ASCE/SEI 7-10 including Supplement No. 1 for 2012 IBC] [ASCE/SEI 7-10 including Supplement No. 1 for 2015 IBC] [ASCE/SEI 7-16 for 2018 IBC] <Insert ASCE/SEI 7 Edition> or as required by authorities having jurisdiction.

          - Vibration Isolator, Seismic[ and Wind Load] Restraint, and Vibration Isolation Base Selection: Select vibration isolators, seismic[ and wind load] restraints, and vibration isolation bases complying with performance requirements, design criteria, and analysis data.

          - Riser Supports: Include riser diagrams and calculations showing anticipated expansion and contraction at each support point, initial and final loads on building structure, spring deflection changes, and seismic loads. Include certification that riser system was examined for excessive stress and that none exists.

          - All delegated-design submittals are to be signed and sealed by the qualified professional engineer responsible for their preparation.

Retain "Seismic Design Calculations" Paragraph below if design services have been delegated to Contractor.

        - Seismic Design Calculations:

ASCE/SEI 7 is generally applicable in most locations, but it is the HVAC engineer's responsibility to determine the applicable building codes and editions thereof, and applicable seismic design standards that apply to this Project. Data and information required for seismic calculations in ASCE/SEI 7 are listed below. ASCE/SEI 7-05 (2005), 7-10 (2010), and 7-16 (2016) differ somewhat; material from all three editions has been included below and has been noted. The HVAC engineer must delete all inappropriate editions throughout the Section.

          - Calculations must be performed to obtain force information necessary to properly select seismic restraint devices, fasteners, and anchorage. Calculations are to be performed using methods acceptable to IBC and as presented in the applicable edition of [ASCE 7-05] [ASCE/SEI 7-10] [ASCE/SEI 7-16] [ or as otherwise acceptable to authorities having jurisdiction]. Data indicated below that are specific to individual pieces of equipment must be obtained by the Contractor, and must be included in individual component submittal packages.

Data values identified below as applying to all components on the Project are to be inserted by the HVAC engineer into these specifications where indicated in the following list. Data values that are specific to an individual generic component and are indicated to be scheduled should be included by the HVAC engineer on the HVAC Vibration-Control and Seismic Restraint Device Schedule or the individual component schedules on the Drawings. Data values that are specific to an individual piece of equipment as provided by the Contractor and are indicated to be obtained by the Contractor must be included in individual component submittal packages.

Retain first subparagraph below if ASCE/SEI 7-16 applies to this Project.

          - The following calculation factors refer to ASCE/SEI 7-16, Chapter 13 - Seismic Design Requirements for Nonstructural Components. All Section, Paragraph, Equation, and Table numbers refer to ASCE/SEI 7-16 unless otherwise noted.

            - Horizontal Seismic Design Force Fp is calculated by Eq. 13.3-1. Factors below must be obtained for this calculation.

              - SDS = Spectral Acceleration: <Insert value>. (Value applies to all components on the Project. Value obtained by HVAC engineer from Project structural engineer, Section 11.4.5.)

              - ap = Component Amplification Factor: <Insert value>. Schedule for each component. (Varies from 1.00 to 2.50. Selected by HVAC engineer from Table 13.6-1.)

              - Ip = Component Importance Factor: Schedule for each component. [1.00] [1.50] Assigned by HVAC engineer as explained in Editing Instruction document and in Sec. 13.1.3 (value 1.00 or 1.50).

              - Wp = Component Operating Weight: Obtained by Contractor from each component submittal.

              - Rp = Component Response Modification Factor: Schedule for each component. (Varies from 1.00 to 12.  Selected by HVAC engineer from Table 13.6-1.)

              - z = Height in structure of point of attachment of component with respect to the base. Determined from Project Drawings for each component by Contractor. For items at or below the base, z shall be taken as 0.

              - h = Average roof height of structure with respect to the base. Determined from Project Drawings by Contractor.

            - In lieu of seismic design forces, dynamic analysis may be used as defined in Para. 13.3.1.4 where applicable and approved by authorities having jurisdiction.

            - Seismic Relative Displacement Dp is calculated using methods explained in Para. 13.3.2. Factors below must be obtained for this calculation.

              - Dp = Relative seismic displacement that the component must be designed to accommodate - calculated in accordance with Para. 13.3.2.

              - Ie = Structure Importance Factor: <Insert value>. Value applies to all components on the Project. Value obtained by HVAC engineer from project structural engineer, Sec. 11.5.1.

              - δxA = Deflection at building level x of structure A: Schedule for each component. Value is determined in accordance with Eq. 12.8-15 and depends upon location of component in the building. Value obtained by HVAC engineer from Project structural engineer.

              - δyA = Deflection at building level y of structure A: Schedule for each component. Value is determined by HVAC engineer from Project structural engineer in accordance with Eq. 12.8-15 and depends upon location of component in the building.

              - δyB = Deflection at building level y of structure B: Schedule for each component. Value is determined in accordance with Eq. 12.8-15 and depends upon location of component in the building. Value is obtained by HVAC engineer from Project structural engineer.

              - hx = Height of level x to which upper connection point is attached:  Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - hy = Height of level y to which upper connection point is attached:  Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - ΔaA = Allowable story drift for structure A: Schedule for each component. <Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by HVAC engineer from Project structural engineer.

              - ΔaB = Allowable story drift for structure B: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by HVAC engineer from Project structural engineer.

              - hsx = Story height used in the definition of the allowable drift Δa: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by HVAC engineer from Project structural engineer.

            - Component Period Dpl is calculated using methods explained in Para. 13.3.3. Factors below must be obtained for this calculation.

              - Tp = Component fundamental period: Determined by Contractor from Project Drawings and manufacturer's data.

              - Wp = Component operating weight: Determined by Contractor from Project Drawings and manufacturer's data.

              - g = Gravitational Acceleration - [32.17 ft./sec2 (9.81 m/sec2)] <Insert ft./sec2 (m/sec2)>.

              - Kp = Combined stiffness of the component, supports, and attachments: Determined by delegated-design seismic engineer.

Retain first subparagraph below if ASCE/SEI 7-10 applies to this Project.

          - The following calculation factors refer to ASCE/SEI 7-10, Chapter 13 - Seismic Design Requirements for Nonstructural Components. All Section, Paragraph, Equation, and Table numbers refer to ASCE/SEI 7-10 unless otherwise noted.

            - Horizontal Seismic Design Force Fp is calculated by Eq. 13.3-1. Factors below must be obtained for this calculation.

              - SDS = Spectral Acceleration: <Insert value> Value applies to all components on the Project. Value obtained by HVAC engineer from Project structural engineer, Section 11.4.5.

              - ap = Component Amplification Factor: Schedule for each component. Varies from 1.00 to 2.50. Selected by HVAC engineer from Table 13.6-1.

              - Ip = Component Importance Factor: Schedule for each component. [1.00] [1.50] Assigned by HVAC engineer as explained in Editing Instruction document and in Sec. 13.1.3 (value 1.00 or 1.50).

              - Wp = Component Operating Weight Obtained by Contractor for each component from equipment submittal.

              - Rp = Component Response Modification Factor: Schedule for each component. Varies from 1.00 to 12. Selected by HVAC engineer from Table 13.6-1.

              - z = Height in structure of point of attachment of component with respect to the base. Determined from Project Drawings for each component by Contractor. For items at or below the base, z shall be taken as 0.

              - h = Average roof height of structure with respect to the base: Determined from Project Drawings by Contractor.

            - In lieu of seismic design forces, accelerations may be determined by the modal analysis procedures of Section 12.9 as set forth in Para. 13.3.1 where applicable and approved by authorities having jurisdiction.

            - Seismic Relative Displacement Dpl is calculated using methods explained in Para. 13.3.2. Factors below must be obtained for this calculation.

              - Dp = Relative seismic displacement that the component must be designed to accommodate - calculated in accordance with Para. 13.3.2.

              - Ie = Structure Importance Factor: <Insert value> Value applies to all components on the Project. Value obtained by HVAC engineer from Project structural engineer, Sec. 11.5.1.

              - δxA = Deflection at building level x of structure A: Schedule for each component. Value is determined in accordance with Eq. 12.8-15 and depends upon location of component in the building. Value obtained by HVAC engineer from Project structural engineer.

              - δyA = Deflection at building level y of structure A: Schedule for each component. Value is determined in accordance with Eq. 12.8-15 and depends upon location of component in the building. Value obtained by HVAC engineer from Project structural engineer, Section 11.4.5.

              - δyB = Deflection at building level y of structure B: Schedule for each component. Value is determined in accordance with Eq. 12.8-15 and depends upon location of component in the building. Value obtained by HVAC engineer from Project structural engineer, Section 11.4.5.

              - hx = Height of level x to which upper connection point is attached:  Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - hy = Height of level y to which upper connection point is attached: Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - ΔaA = Allowable story drift for structure A: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value obtained by HVAC engineer from Project structural engineer, Section 11.4.5.

              - ΔaB = Allowable story drift for structure B: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value obtained by HVAC engineer from Project structural engineer, Section 11.4.5.

              - hsx = Story height used in the definition of the allowable drift Δa: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value obtained by HVAC engineer from Project structural engineer, Section 11.4.5.

Retain first subparagraph below if ASCE 7-05 applies to this Project.

          - The following calculation factors refer to ASCE 7-05, Chapter 13 - Seismic Design Requirements for Nonstructural Components. All Section, Paragraph, Equation, and Table numbers refer to ASCE 7-05 unless otherwise noted.

            - Horizontal Seismic Design Force Fp is calculated by Eq. 13.3-1. Factors below must be obtained for this calculation.

              - SDS = Spectral Acceleration: <Insert value> Value applies to all components on the Project. Value is obtained by HVAC engineer from project structural engineer, Section 11.4.4.

              - ap = Component Amplification Factor: Schedule for each component. Varies from 1.00 to 2.50. Selected by HVAC engineer from Table 13.6-1.

              - Ip = Component Importance Factor: Schedule for each component [1.00] [1.50]. Assigned by HVAC engineer as explained in Editing Instructions document and in Section 13.1.3 (value 1.00 or 1.50).

              - Wp = Component Operating Weight: Obtained by Contractor from each component submittal.

              - Rp = Component Response Modification Factor: Schedule for each component. Varies from 1.00 to 12. Selected by HVAC engineer from Table 13.6-1.

              - z = Height in structure of point of attachment of component with respect to the base: Determined from Project Drawings for each component by Contractor.  For items at or below the base, z shall be taken as 0.

              - h = Average roof height of structure with respect to the base. Determined from Project Drawings by Contractor.

            - Alternate calculation method with Eq. 13.3-4 may be used as indicated in Section 13.3.1 where applicable and approved by authorities having jurisdiction.

            - Seismic Relative Displacement Dp is calculated using methods explained in Para. 13.3.2. Factors below must be obtained for this calculation.

              - δxA = Deflection at building level x of structure A: Schedule for each component. Value is determined as defined in Section 12.8.6 and depends upon location of component in the building. Value obtained by HVAC engineer from Project structural engineer.

              - δyA = Deflection at building level y of structure A: Schedule for each component. Value is determined as defined in Section 12.8.6 and depends upon location of component in the building. Value is obtained by HVAC engineer from Project structural engineer.

              - δyB = Deflection at building level y of structure B: Schedule for each component. Value is determined as defined in Section 12.8.6 and depends upon location of component in the building. Value is obtained by HVAC engineer from Project structural engineer.

              - hx = Height of level x to which upper connection point is attached: Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - hy = Height of level y to which upper connection point is attached: Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - ΔaA = Allowable story drift for structure A: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by HVAC engineer from Project structural engineer.

              - ΔaB = Allowable story drift for structure B: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by HVAC engineer from Project structural engineer.

              - hsx = Story height used in the definition of the allowable drift Δa: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by HVAC engineer from Project structural engineer.

        - Wind Load Design Calculations

ASCE/SEI 7 is generally applicable in most locations, but it is the HVAC engineer's responsibility to determine the applicable building codes and editions thereof, and applicable wind load design standards that apply to this Project. Data and information required for wind load calculations in ASCE/SEI 7 are listed below. ASCE/SEI 7-05 (2005), 7-10 (2010), and 7-16 (2016) differ somewhat; material from all three editions has been included below and has been noted. The HVAC engineer must delete all inappropriate editions throughout the Section.

          - Calculations must be performed to obtain force information necessary to properly select wind load restraint devices, fasteners, and anchorage. Calculations are to be performed using methods acceptable to IBC and as presented in the applicable edition of [ASCE 7-05] [ASCE/SEI 7-10] [ASCE/SEI 7-16] [or as otherwise acceptable to authorities having jurisdiction]. Data indicated below that are specific to individual pieces of equipment must be obtained by the Contractor, and must be included in individual component submittal packages.

Data values identified below as applying to all components on the Project are to be inserted by the HVAC engineer into these Specifications where indicated in the following list.  Data values that are specific to an individual generic component and are indicated to be scheduled should be included by the HVAC engineer on the HVAC Vibration-Control and Seismic Restrain Device Schedule or the individual component schedules on the Drawings. Data values that are specific to an individual piece of equipment as provided by the Contractor and are indicated to be obtained by the Contractor must be included in individual component submittal packages.

Retain first subparagraph below if ASCE/SEI 7-16 applies to this Project.

          - The following calculation factors refer to ASCE/SEI 7-16, Chapters 26 -Wind Loads: General Requirements, Chapter 29 - Wind Loads on Building Appurtenances, and Chapter 30 - Wind Loads: Components and Cladding. All Section, Paragraph, Equation, and Table numbers refer to ASCE/SEI 7-16 unless otherwise noted.

Retain first subparagraph below if ASCE/SEI 7-10 applies to this Project.

          - The following calculation factors refer to ASCE/SEI 7-10, Chapter 26 -Wind Loads: General Requirements, Chapter 29 - Wind Loads on Other Structures and Building Appurtenances, and Chapter 30 - Wind Loads - Components and Cladding. The factors and calculation methods for rooftop equipment on buildings not over 60 ft. (18.3 m) are the same as those in ASCE/SEI 7-16. ASCE/ASI 7-10 does not provide any standards for buildings over 60 ft. (18.3 m). Wind load designer must use calculation methods acceptable to the authorities having jurisdiction.

Retain first subsection below if either ASCE/SEI 7-16 or ASCE/SEI 7-10 applies to this Project.

            - Horizontal Design Wind Load Fh and Vertical Wind Uplift Force Fv for rooftop equipment are calculated by Eq. 9.4-2. Factors below must be obtained for this calculation.

              - Risk Category: [I] [II] [III] [IV]. Value applies to all rooftop equipment on building - obtained by HVAC engineer from Project Architect as explained in Section 1.5 and Table 1.5-1.

              - V = Basic Wind Speed: <Insert value> from Wind Hazard map in ASCE/SEI 7 or other approved source.

              - Kd = Wind directionality factor: <Insert factor> Value obtained by HVAC engineer from Sec. 26.6 and Table 26.6-1.

              - Exposure Category: [B] [C] [D] from Sec. 26.7. Value obtained by HVAC engineer.

              - Kzt = Topographic Factor: <Insert factor>. Value obtained by HVAC engineer from Sec. 26.8 and Table 26.8-1.

              - Ke = Ground Elevation Factor: <Insert factor>. Value obtained by HVAC engineer from Sec. 26.8 and Table 26.8-1.

              - Enclosure classification: <Insert classification>. Value obtained by HVAC engineer from Sec. 26.12.

              - GCpi = Internal pressure coefficient: <Insert coefficient>. Value obtained by HVAC engineer from Table 26.13-1.

              - Kz = Velocity pressure exposure coefficient: <Insert coefficient> Value obtained by HVAC engineer from Sec. 26.10.1.

              - Kh = Velocity pressure exposure coefficient: <Insert coefficient>. Value obtained by HVAC engineer from Sec. 26.10.1.

              - qz = Velocity pressure: <Insert lb/sq. ft. (N/sq. m)>. Value calculated by delegated wind load design contractor.

              - qh = Velocity pressure: <Insert lb/sq. ft. (N/sq. m)>. Value calculated by delegated wind load design contractor.

              - GCr = Gust factor for roof-mounted equipment: <Insert factor>. Value obtained by HVAC engineer from Sec. 29.4.1.

              - Af = Vertical projected area of rooftop equipment on a plane normal to the direction of wind <Insert sq. ft. (sq. m)>. Values obtained by contractor from equipment manufacturer.

              - Ar = Horizontal projected area of rooftop equipment <Insert sq. ft. (sq. m)>. Value obtained by Contractor from equipment manufacturer.

            - Design Wind Pressure p for external sidewall mounted equipment such as louvers is calculated using the methods in ASCE/SEI 7-16, Chapter 30. The methods differ for low-rise, mid-rise h < 60 ft. (h < 18.3 m), and high-rise 60 ft. < h < 160 ft. (18.3 m < h < 48.8 m). Within each height category, calculation methods also differ because of building shape and other factors. The required calculation factors and equations are found in Chapter 30.

Retain first subparagraph below if ASCE 7-05 applies to this Project.

          - The following calculation factors refer to ASCE 7-05, Chapter 6 - Wind Loads. All Section, Paragraph, Equation, and Table numbers refer to ASCE 7-05 unless otherwise noted.

            - F = Design wind load for rooftop equipment. Calculated by delegated wind load design contractor using methods presented in ASCE 7-05, Chapter 6.

            - qz = Velocity pressure calculated by delegated wind load design contractor.

            - G = Gust effect factor: 0.85. Value obtained by HVAC engineer - value may be calculated as presented in Para. 6.5.8.

            - Cf = Force coefficient: <Insert factor>. Value obtained by HVAC engineer from Figure 6-20.

            - Af = Projected area normal to the wind (except when Cf is adjusted for actual surface area sq. ft. (sq. m): Value calculated by delegated wind load design contractor using wind data found in ASCE 7-05 and equipment dimension data supplied by equipment manufacturer.

Retain "Seismic(- and Wind)-Restraint Details" Subparagraph below only if design requirements apply but calculations have not been made and details or charts on Drawings do not describe seismic or wind restraints in detail. Retaining subparagraph requires Contractor to submit seismic-restraint delegated-design Drawings prepared by a professional engineer. Revise to suit local requirements.

          - Seismic[- and Wind]-Restraint Details:

            - Design Analysis: To support selection and arrangement of seismic[ and wind] restraints. Include calculations of combined tensile and shear loads.

            - Details: Indicate fabrication and arrangement. Detail attachments of restraints to the restrained items and to the structure. Show attachment locations, methods, and spacings. Identify components, list their strengths, and indicate directions and values of forces transmitted to the structure during seismic events. Indicate association with vibration isolation devices.

Retain first subparagraph below if Project includes equipment mounted outdoors, or otherwise subject to wind loading.

            - Coordinate seismic-restraint and vibration isolation details with wind-restraint details required for equipment mounted outdoors. Comply with requirements in other Sections for equipment mounted outdoors.

            - Product Listing, Preapproval and Evaluation Documentation: By [an evaluation service member of ICC-ES] [FM] [OSHPD] [UL] [an agency acceptable to authorities having jurisdiction], showing maximum ratings of restraint items and the basis for approval (tests or calculations).

      - INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

        - Coordination Drawings: Show coordination of vibration isolation device installation and seismic bracing for HVAC piping and equipment with other systems and equipment in the vicinity, including other supports and restraints, if any.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For [professional engineer] [and] [testing agency].

Retain "Welding certificates" Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Assurance" Article.

        - Welding certificates.

Retain option in "Air-Spring System Performance Certification" Paragraph below if authorities having jurisdiction require independent testing.

        - Air-Spring System Performance Certification: Include natural frequency, load, and damping test data[ performed by an independent agency].

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing.

        - Field quality-control reports.

Include "Special Certification of Designated Seismic Systems" Paragraph in all Specification Sections that specify Designated Seismic Systems, or as required by authorities having jurisdiction.

        - Special Certification of Designated Seismic Systems: Provide special certification for all Designated Seismic Systems assigned to Seismic design Categories C through F. Designated Seismic Systems include:

          - All active nonstructural mechanical equipment that must remain operable following the design earthquake ground motion. This equipment is assigned an Importance Factor greater than 1.0.

          - Components with hazardous substances and assigned Importance Factor of 1.5.

        - Provide Special Certification of Designated Seismic Systems:

          - Provide manufacturer's written certification that all Designated active mechanical seismic systems will remain operable following the design earthquake. Certification must be based on requirements of ASCE/SEI 7 and ANSI/AHRI 1270 (I-P) or ANSI/AHRI 1271 (SI), including shake table testing as per ICC-ES AC156 or a similar nationally recognized testing standard procedure acceptable to the authority having jurisdiction or experience data as permitted by ASCE/SEI 7.

          - Provide manufacturer's written certification that components with hazardous contents maintain containment following the design earthquake by methods required in ASCE/SEI 7.

          - Submit evidence demonstrating compliance with these requirements for approval to the authority having jurisdiction after review and acceptance by a licensed professional engineer.

            - Active HVAC designated seismic systems are those with parts that rotate, move mechanically or are energized during operation unless they are considered rugged.

            - HVAC components that contain motors of greater than 10 hp or have a thermal exchange greater than 200 MBH are not rugged.

            - HVAC piping and ductwork is not active and does not require AC 156 shake table testing.

            - HVAC active designated seismic systems for which experience data for seismic qualification that is acceptable to the authority have jurisdiction does not require AC 156 shake table testing.

Retain subparagraph below only if Designated Seismic Systems are not scheduled. If a schedule is not being used, all Designated Seismic Systems must be listed below. See "Special Certification Requirements for Active Designated Seismic Systems" paragraph in the Evaluations for more information and a list of potential designated systems.

          - The following HVAC systems and components are Designated Seismic Systems and require written special certification of seismic qualification by manufacturer;

            - <Insert list>

      - CLOSEOUT SUBMITTALS

Retain this article for restrained air-spring isolators.

        - Operation and Maintenance Data: For [air-spring mounts] [and] [restrained-air-spring mounts] to include in operation and maintenance manuals.

      - QUALITY ASSURANCE

If an independent testing agency is required, see Section 014000 "Quality Requirements" for general testing and inspecting agency qualification requirements. If additional control is needed, retain "Testing Agency Qualifications" Paragraph below to specify 29 CFR 1910.7. 29 CFR 1910.7 defines "NRTL" (nationally recognized testing laboratory) as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that comply with certain OSHA criteria.

Retain "Testing Agency Qualifications" Paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.

        - Testing Agency Qualifications: An independent agency, with the experience and capability to conduct the testing indicated, that is an NRTL as defined by OSHA in 29 CFR 1910.7 and that is acceptable to authorities having jurisdiction.

        - Comply with seismic-restraint[ and wind load] requirements of all applicable codes and authorities having jurisdiction unless requirements in this Section are more stringent.

        - Comply with the requirements of [ASCE 7-05 for 2009 IBC] [ASCE/SEI 7-10 including Supplement No. 1 for 2012 IBC] [ASCE/SEI 7-10 including Supplement No. 1 for 2015 IBC] [ASCE/SEI 7-16 for 2018 IBC] <Insert ASCE/SEI 7 Edition> for anchorage to concrete, including the effects of prying, unless the requirements of the applicable edition of the IBC or this Section are more stringent.

Retain first subparagraph below if ASCE/SEI 7-05 is selected in paragraph above.

          - Anchorage to concrete or masonry shall be proportioned to carry 1.3 times the calculated seismic load.

Retain first subparagraph below if ASCE/SEI 7-10 is selected in paragraph above.

          - Overstrength value for determining concrete anchor capacity in ASCE/SEI 7-10, Supplement No. 1 need not be taken as greater than 2.0.

Retain first subparagraph below if ASCE/SEI 7-16 is selected in paragraph above.

          - Overstrength value for determining concrete anchor capacity in ASCE/SEI 7-10, Supplement No. 1 need not be taken as greater than 2.0.

        - Do not use powder-actuated fasteners in concrete or steel for hanging or bracing in Seismic Design Category D, E or F or in masonry in any Seismic Design Category, unless approved for seismic loading.

        - Friction Clips:

Retain first subparagraph below if ASCE/SEI 7-05 is selected.

          - Component attachments shall be bolted, welded, or otherwise positively fastened without consideration of friction resistance resulting from the effects of gravity. Friction clips (C-type clamps) shall not be used for anchorage attachment.

Retain subparagraph below if ASCE/SEI 7-10 or ASCE/SEI 7-16 is selected.

          - Component attachments shall be bolted, welded or otherwise positively fastened without consideration of friction resistance resulting from the effects of gravity. Friction clips (C-Type beam clamps) shall not be used in Seismic Design Category D, E or F to support permanent loads in addition to seismic loads. C-type clamps are permitted for fastening 156 hangers, when they are equipped with retaining straps, equivalent to those specified in NFPA 13, and locknuts are provide to prevent loosening of threaded connections.

Retain "Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

        - Welding Qualifications: Qualify procedures and personnel in accordance with AWS D1.1/D1.1M, "Structural Welding Code - Steel."

        - Comply with requirements of [ASCE/SEI 19-96 for 2009 IBC] [ASCE/SEI 19-10 for 2012 IBC] [ASCE/SEI 19-10 for 2015 IBC] [ASCE/SEI 19-16 for 2018 IBC] <Insert ASCE/SEI 19 Edition> for steel cable assemblies used for Seismic Restraints - Cable Type.

        - Seismic restraint devices shall have load ratings based on testing conducted in accordance with IBC referenced standards and listed by a nationally recognized third party that requires periodic follow-up inspections and a has a listing directory available to the public. Third party listing shall be by [ICC-ES Product Listing] [UL Product Listing] [FM Approvals] [an evaluation service member of ICC-ES] [an agency acceptable to authorities having jurisdiction].

        - Calculations (including combining shear and tensile loads) to support seismic-restraint designs must be signed and sealed by a qualified professional engineer.

        - Consequential Damage: Provide additional seismic restraints for suspended HVAC components or anchorage of floor-, roof- or wall-mounted HVAC components so that failure of a non-essential or essential HVAC component will not cause the failure of any other essential architectural, mechanical, or electrical building component.

        - Fire/Smoke Resistance: Seismic[ and wind load] restraint devices that are not constructed of ferrous metals shall comply with IMC 602, maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested by an NRTL in accordance with ASTM E84 or UL 723, and be so labeled.

- PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

See the Evaluations for more detailed information about controlling vibration, additional information on products described in this Section, illustrations, selection guides, and supplements to equipment schedules.

Coordinate specifications for products in this Section with structural engineer and with Drawings.

      - PERFORMANCE REQUIREMENTS

        - Building ["Occupancy Category" for 2009 IBC] ["Risk Category" for 2012, 2015 or 2018 IBC], Category [I] [II] [III] [IV].

        - Site Class as defined in ASCE/SEI 7: [A] [B] [C] [D] [E] [F].

        - Seismic design shall be based on the methods presented in [ASCE 7-05] [ASCE/SEI 7-10] [ASCE/SEI 7-16].

        - Horizontal Seismic Design Force: HVAC components shall be designed to resist horizontal earthquake force (Fp), as defined in ASCE/SEI 7, applied at the center of gravity of the component and shall consider both upward and downward vertical forces.

        - Vertical Seismic Design Force: HVAC components shall be designed to resist both upward and downward vertical forces resulting from the application of the horizontal seismic design force plus a concurrent vertical force equal to 0.2 SDSD, as defined in ASCE/SEI 7.

        - Select appropriate seismic coefficients from ASCE/SEI 7, Table 13.6-1.

        - Allowable Stresses on Pipe and Tube:

          - Unless piping or tubing is designed with flexible connections that will avoid component failure at component connections, or components such as valves, strainers, traps, pumps, air separators, and tanks are mounted inline and laterally braced as part of the pipe or tube, or components are braced independently, because of their weight, with flexible connections to components, then the pipe or tube, other than ASME pressure piping, shall be designed based on the following allowable stresses.

            - 90 percent of the minimum yield strength for ductile piping, such as steel, aluminum or copper, with welded or brazed connections.

            - 70 percent of the minimum yield strength for ductile piping, such as steel, aluminum or copper, with threaded, bonded, compression coupling or grooved coupling connections.

            - 10 percent of the minimum yield strength for nonductile piping, such as cast iron or ceramics, with compression coupling or grooved coupling connections.

            - 8 percent of the minimum yield strength for nonductile piping with threaded connections.

          - ASME Pressure Piping Systems and NFPA 13 Piping Systems: Pressure piping systems and other piping systems, including their supports, designed and constructed in accordance with ASME B31 or NFPA 13, shall be deemed to meet the seismic requirements of this Section.

Retain first paragraph below if using ASCE 7-05.

        - Exceptions to the Seismic Protection Requirements of this Section for HVAC Components based on Component Importance Factor (Ip) and Seismic Design Category: The following HVAC components are exempt from the seismic design requirements of ASCE 7-05.

          - All HVAC components in Seismic Category B.

          - HVAC components in Seismic Design Category C where the Component Importance Factor (Ip) equals 1.0.

          - HVAC components in Seismic Design Category D, E, or F where the Component Importance Factor (Ip) equals 1.0 and either:

            - Flexible connections between the components and associated ductwork, piping, or conduit are provided, or

            - Components are mounted at 4 ft. (1.22 m) or less above a floor level and weigh 400 lb (1780 N) or less.

          - HVAC components in Seismic Design Category D, E or F where the Component Importance Factor (Ip) equals 1.0 and:

            - Flexible connections between the components and associated duct work, piping, and conduits are provided, and

            - The components weigh 20 lb (89 N) or less or, for distribution systems, weigh 5 lb/ft. (73 N/m) or less.

Retain first paragraph below if using ASCE/SEI 7-10.

        - Exceptions to the seismic protection requirements of this Section for HVAC components based on Component Importance Factor (Ip) and Seismic Design Category: The following HVAC components are exempt from the seismic design requirements of ASCE/SEI 7-10.

          - HVAC components in Seismic Design Category B.

          - HVAC components in Seismic Design Category C where the Component Importance Factor (Ip) equals 1.0.

          - HVAC components in Seismic Design Category D, E, or F where all the following apply.

            - The Component Importance Factor (Ip) equals 1.0.

            - The component is positively attached to the structure.

            - Flexible connections are provided between the component and associated ductwork, piping, and conduit, and the component either:

              - Weighs 400 lb (1780 N) or less and has a center of mass located 4 ft. (1.22 m) or less above the adjacent floor lever; or

              - Weighs 20 lb (89 N) or less or, in the case of a distributed system, 5 lb/ft. (73 N/m) or less.

Retain first paragraph below if using ASCE/SEI 7-16.

        - Exceptions to the seismic protection requirements of this Section for HVAC components based on Component Importance Factor (Ip) and Seismic Design Category: The following HVAC components are exempt from the seismic design requirements of ASCE/SEI 7-16.

          - HVAC components in Seismic Design Category B.

          - HVAC components in Seismic Design Category C provided that either:

            - The Component Importance Factor (Ip) equals 1.0 and the component is positively attached to the structure; or

            - The component weighs 20 lb (89 N) or less, or where the component is a distribution system (pipe, duct, etc.) weighing 5 lb/ft. (73 N/m) or less.

          - HVAC components in Seismic Design Category D, E, or F where the component are positively attached to the structure provided that either:

            - The component weighs 400 lbs (1779 N) or less, the component center of mass is 4 ft. (1220 mm) or less above the floor, flexible connections are provided between the component and any associated ductwork, piping, or conduit, and the Component Importance Factor (Ip) equals 1.0; or

            - The component weighs 20 lb (89 N) or less, or where the component is a distribution system (pipe, duct, etc.) weighing 5 lb/ft. (73 N/m) or less.

          - Distribution systems in Seismic Design Category D, E, or F that do not carry toxic, highly toxic, or flammable substances, utilize flexible connections to other separately mounted systems, and are positively attached to the structure, provided that they meet all other exemption requirements of ASCE/SEC 7-16. Where in-line components, such as valves, inline suspended pumps, and air handling devices require independent support, they shall be addressed as discrete components and shall be braced considering the tributary contribution of the attached distribution system.

        - Exceptions Based on Component Size or Method of Attachment: The following HVAC components are exempt from the seismic design requirements of this Section:

Retain first subparagraph below if using ASCE/SEI 7-05.

          - The following exceptions from the seismic protection requirements of this Section are for HVAC and other ducts that are not used for smoke control and do not carry toxic or flammable gasses:

            - HVAC ducts with Ip = 1.0 where one of the following applies:

              - Ducts supported by individual hanger rods not exceeding 12 in. (305 mm) in length and the hanger rods are equipped with swivels to prevent bending of the rod.

              - Ducts with a cross-sectional area of less than 6 sq. ft. (0.557 sq. m).

            - HVAC ducts that are fabricated and installed in accordance with standards approved by the authority having jurisdiction shall be deemed to meet the seismic bracing requirements of this Section.

            - Components, such as VAV boxes, fans, heat exchangers, and humidifiers, that are installed in line with the duct and weighing more than 75 lb. (334 N), shall be supported and seismically braced in accordance with this Section.

            - Appurtenances, such as dampers, louvers, and diffusers, shall be positively attached with mechanical fasteners and any unbraced piping attached to in-line equipment shall be equipped with flexible connections.

          - The following exceptions from the seismic protection requirements of this Section are for pipe and tube systems:

            - Pipe or tube, regardless of pipe size or Seismic Design Category, that is supported by single rod hangers, where every hanger on the pipe run is equal to or less than 12 in. (305 mm) in length from the top of the pipe to the point to the connection to the structure and:

              - The hanger rods are equipped with swivels, eye nuts, or other device that prevents bending of the rod or attachments and

              - Provision is made to accommodate deflections.

            - Pipe or tube, when provisions are made to avoid impact with other larger piping or mechanical components, or to protect it from such impact, and the pipe does not exceed the following sizes:

              - 2 in. (50 mm) or less nominal pipe size in Seismic Design Category C.

              - 1 in. (25 mm) or less nominal pipe size in Seismic Design Category C, D, E or F.

              - 3 in. (80 mm) or less nominal pipe size with Ip = 1.0 in Seismic Design Category C, D, E or F.

Retain first subparagraph below if using ASCE/SEI 7-10.

          - The following exceptions from the seismic protection requirements of this Section are for HVAC and other ducts that are not used for smoke control and do not carry toxic or flammable gasses:

            - HVAC ducts with Ip = 1.0 where one of the following applies:

              - Trapeze assemblies are used to support the ductwork and total weight supported by the trapeze assemblies is less than 10 lb/ft. (146 N).

              - HVAC ducts supported by individual hanger rods not exceeding 12 in. (305 mm) in length from the duct support point to the connection to the structure and the hanger rods are equipped with swivels to prevent bending of the rod.

            - Where provisions are made to avoid impact with larger ducts or mechanical components or to protect the ducts in the event of such impact and the duct has a cross-sectional area less than 6 sq. ft. (0.557 sq. m) or the duct weighs 17 lb/ft. (248 N/m) or less.

            - HVAC ducts that are fabricated and installed in accordance with standards approved by the authority having jurisdiction shall be deemed to meet the seismic bracing requirements of this Section.

            - Components, such as VAV boxes, fans, heat exchangers and humidifiers that are installed in line with the duct and weighing more than 75 lb (334 N), shall be supported and seismically braced in accordance with this Section.

            - Appurtenances, such as dampers, louvers, and diffusers, shall be positively attached with mechanical fasteners and any unbraced piping attached to in-line equipment shall be equipped with flexible connections.

          - The following exceptions from the seismic protection requirements of this Section are for pipe and tube systems:

            - Pipe and tube supported by single rod hangers or trapeze supports, where every hanger on the pipe run is equal to or less than 12 in. (305 mm) in length from the top of the pipe, or the pipe support point for trapeze supports, to the point to the connection to the structure and the hanger rods are equipped with swivels, eye nuts, or other device that prevents bending of the rod.

            - Pipe and tube are exempt from the seismic protection requirements of this Section, where no single pipe exceeds the following sizes:

              - 2 in. (50 mm) or less nominal pipe size in Seismic Design Category C.

              - 1 in. (25 mm) or less nominal pipe size in Seismic Design Category C, D, E, or F.

              - 3 in. (80 mm) or less nominal pipe size with Ip = 1.0 in Seismic Design Category C, D, E, or F.

              - When:

                - Trapeze assemblies are used to support the piping and the total weight of the pipe supported by the trapeze is less than 10 lb/ft. (146 N/m). or

                - Piping with Rp greater than or equal to 4.5 and provisions are made to avoid impact with other structural or nonstructural building components or to protect it from such impact.

Retain first subparagraph below if using ASCE/SEI 7-16.

          - The following exceptions from the seismic protection requirements of this Section are for HVAC and other ducts that are not used for smoke control and do not carry toxic or flammable gasses:

            - HVAC and other ducts with Ip = 1.0 where flexible connections are provided between the duct and associated equipment; the duct is positively attached to the structure and one of the following apply:

              - Trapeze assemblies with 3/8 in. (10 mm) dia. hanger rods not exceeding 12 in. (305 mm) in length from the duct support point to the connection to the structure and total weight supported by any one trapeze is less than 10 lb/ft. (146 N).

              - Trapeze assemblies with 1/2 in. (13 mm) dia. hanger rods not exceeding 12 in. (305 mm) in length from the duct support point to the connection to the structure and total weight supported by any one trapeze is 200 lb/ft. (890 N) or less.

              - Trapeze assemblies with 1/2 in. (13 mm) dia. hanger rods not exceeding 24 in. (610 mm) in length from the duct support point to the connection to the structure and total weight supported by any one trapeze is 100 lb/ft. (445 N) or less.

              - HVAC and other ducts supported by individual hanger rods 3/8 in. (10 mm) or 1/2 in. (13 mm) dia. not exceeding 12 in. (305 mm) in length from the duct support point to the connection to the structure and total weight supported by any one rod is 50 lb/ft. (220 N) or less.

            - HVAC and other ducts: Where provisions are made to avoid impact with other ducts or mechanical components or to protect them in the event of such impact with other ducts or mechanical components or to protect them in the event of such impact, the duct is positively attached to the structure, and the duct has a cross-sectional area less than 6 sq. ft. (0.557 sq, m) and the duct weighs 20 lb/ft. (292 N/m) or less.

            - HVAC Components, such as small terminal units, dampers, louvers and diffusers, that are installed in line with the duct and weighing less than 75 lb (334 N), shall be positively attached to the rigid duct on both sides and any piping or conduit connected to these components shall be flexible connections.

            - Components, such as VAV boxes, fans, terminal units, heat exchangers and humidifiers, that are installed in line with the duct and weighing more than 75 lb (334 N), shall be supported and seismically braced in accordance with this Section.

          - The following exceptions from the seismic protection requirements of this Section are for pipe and tube systems, where flexible connections, expansion loops, or other flexible connection assemblies are provided between the component and the pipe or tube, and the pipe or tube is positively attached to the structure and no single pipe exceeds the following sizes:

            - 2 in. (50 mm) or less nominal pipe size in Seismic Design Category C.

            - 1 in. (25 mm) or less nominal pipe size in Seismic Design Category C, D, E, or F.

            - 3 in. (80 mm) or less nominal pipe size with Ip = 1.0 in Seismic Design Category C, D, E, or F.

            - When: one of the following applies:

              - Trapeze assemblies are used to support the piping and the total weight of the pipe supported by the trapeze is less than 10 lb/ft. (146 N/m); or

              - Trapeze assemblies are used to support the piping with 3/8 in. (10 mm) rods equal to or less than 12 in. (305 mm) in length from the pipe support point to the connection to the structure and a total weight on any one trapeze is 100 lb (445 N) or less; or

              - Trapeze assemblies are used to support the piping with 1/2 in. (13 mm) rods equal to or less than 12 in. (305 mm) in length from the pipe support point to the connection to the structure and a total weight on any one trapeze is 200 lb (890 N) or less; or

              - Trapeze assemblies are used to support the piping with no pipe having Ip of 1.5 and with 1/2 in. (13 mm) rods equal to or less than 24 in. (610 mm) in length from the pipe support point to the connection to the structure and a total weight on any one trapeze is 100 lb (445 N) or less; or

              - Piping with Rp greater than or equal to 4.5 and:

                - The piping is supported by single rod hangers and provisions are made to avoid impact with other structural or nonstructural building components or to protect it from such impact; or

                - The piping has Ip of 1.0 and is supported by 3/8 in. (10 mm) single rod hangers, where every hanger on the pipe run is equal to or less than 12 in. (305 mm) in length from the pipe support point to the connection to the structure and a total weight on any one hanger is 50 lb (220 N) or less.

              - Pneumatic tube systems supported by trapeze assemblies with 3/8 in. (10 mm) rods equal to or less than 12 in. (305 mm) in length from the tube support point to the connection to the structure and a total weight on any one trapeze is 100 lb (445 N) or less.

              - Pneumatic tube systems supported by 3/8 in. (10 mm) or 1/2 in. (13 mm) single rod hangers, where every hanger on the pipe run is equal to or less than 12 in. (305 mm) in length from the tube support point to the connection to the structure and a total weight on any one hanger is 50 lb (220 N) or less.

              - Trapeze assemblies that support a combination of distribution systems (electrical conduit, raceway, duct, piping, etc.) shall be designed using the most restrictive requirements for the supported distribution systems for the aggregate weight of the supported system. If any distribution system on the trapeze is not exempted, the trapeze shall be braced.

        - Seismic-Restraint Loading:

See the Evaluations for a discussion on seismic-restraint capacities and rating services.

          - Load ratings, features, and applications shall be as defined in ICC-ES Product Listings, UL Product Listings, ICC-ES Evaluation Reports, OSHPD, or an agency acceptable to authorities having jurisdiction.

            - Load ratings for seismic restraint components shall include a minimum safety factor of 2.2.

          - Standard supports, such as ASME B31, NFPA 13, MSS SP-58, or proprietary supports, shall be designed by load rating or for the calculated seismic forces.

          - Mechanical supports, such as structural members, braces, frames, skirts, legs, saddles, pedestals, cables, guys, stays, snubbers, tethers, and elements forged or cast into a mechanical component, shall be designed for the seismic forces and displacements, including displacement between piping supports.

          - The means by which supports are attached to the component, except where cast or forged into the component, including the region of support engagement to the component wall where Ip equals 1.5, shall be designed to accommodate the seismic forces and displacements and to maintain support engagement.

          - The materials comprising supports and the means of attachment to the component, including weak-axis bending of cold-formed steel supports, shall be constructed of materials suitable for the application, including the effects of service conditions, and shall be in conformance with a nationally recognized standard.

          - Reinforcement shall be provided at bolted connections through sheet metal equipment housings as required to transfer seismic loads from the equipment to the structure. The design force shall be taken as 2Fp, if the nominal clearance (air gap) between the equipment support frame and restraint is greater than 0.25 in. (6 mm).

Retain "Wind Restraint Loading" Paragraph below for outdoor equipment.

        - Wind Restraint Loading:

Obtain values for items in subparagraphs below from Project structural engineer or from ASCE/SEI 7.

          - Basic Wind Speed: As defined by wind speed maps in [ASCE/SEI 7-16, Chapter 26] [ASCE/SEI 7-10, Chapter 26] [ASCE 7-05, Chapter 6]. Wind Hazard Map <Insert value> mi/h (m∕s) at 33 ft. (10 m) above ground for Exposure Category C.<Insert value>.

          - Minimum 10 lb/sq. ft. (48.8 kg/sq. m) multiplied by maximum area of HVAC component projected on vertical plane normal to wind direction, and 45 degrees either side of normal.

          - Perform wind loading calculations as per ASCE/SEI 7.

      - ELASTOMERIC ISOLATION PADS

Copy "Elastomeric Isolation Pads" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric isolation pads depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation pad on the same Project. Insert Drawing designation for each elastomeric isolation pad type required. Use these designations on Drawings to identify each product.

For information on CADDY’s "CSBRP Rubber Isolation Pads," see http://www.vimco.biz/filecabinet/vimco/Literature/P-2201.pdf .

        - Elastomeric Isolation Pads: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY, CSBRP Elastomeric Isolation Pads or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Fabrication: Single or multiple layers of sufficient durometer stiffness for uniform loading over pad area.

          - Size: Factory or field cut to match requirements of supported equipment.

Verify availability of various pad materials and their properties with manufacturers.

          - Pad Material: Oil and water resistant with elastomeric properties. [Neoprene rubber.] [Silicone rubber.]

          - Surface Pattern: [Smooth] [Ribbed] [Waffle] pattern.

Retain first subparagraph below if pad is infused with synthetic fibers.

          - Infused nonwoven cotton or synthetic fibers.

Retain first subparagraph below if galvanized-steel baseplates are adhered to the isolation pad to facilitate load distribution.

          - Load-bearing metal plates adhered to pads.

Retain "Sandwich-Core Material" Subparagraph below if pad has a sandwich-core material.

Copy "Sandwich-Core Material" Subparagraph below and re-edit for each sandwich-core material. Core materials may not be elastomeric. See the "Elastomeric Isolation Pads" Article in the Evaluations for more information.

          - Sandwich-Core Material: [Resilient] [and] [elastomeric] <Insert compound>.

Retain "Surface Pattern" Subparagraph below if the sandwich-core material has a surface pattern.

            - Surface Pattern: [Smooth] [Ribbed] [Waffle] pattern.

Retain subparagraph below if pad is infused with synthetic fibers.

            - Infused nonwoven cotton or synthetic fibers.

      - ELASTOMERIC ISOLATION MOUNTS

Copy "Double-Deflection, Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation mount on the same Project. Insert drawing designation for each elastomeric isolation mount type required. Use these designations on Drawings to identify each product.

For information on CADDY’s "CSBRM Rubber Mounts," see http://www.vimco.biz/filecabinet/vimco/Literature/S-2225-01.pdf.

        - Double-Deflection, Elastomeric Isolation Mounts: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBRM Elastomeric Isolation Mounts or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Mounting Plates:

            - Top Plate: Encapsulated steel load transfer top plates, factory drilled and threaded[ with threaded studs or bolts].

Retain "Baseplate" Subparagraph below if the elastomeric mount being specified has a baseplate.

            - Baseplate: Encapsulated steel bottom plates with holes provided for anchoring to support structure.

          - Elastomeric Material: Molded, oil-resistant, [neoprene rubber] [silicone rubber], or other elastomeric material.

      - RESTRAINED ELASTOMERIC ISOLATION MOUNTS

Copy "Restrained Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

The configuration and materials of restrained elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of restrained elastomeric isolation mount on the same Project. Insert drawing designation for each restrained elastomeric isolation mount type required. Use these designations on Drawings to identify each product.

For information on CADDY’s "CSBRSM Rubber Mounts," see http://www.vimco.biz/filecabinet/vimco/Literature/S-3100-61.pdf.

        - Restrained Elastomeric Isolation Mounts: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBRSM Restrained Elastomeric Isolation Mounts or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Description: All-directional isolator with seismic restraints containing two separate and opposing elastomeric elements that prevent central threaded element and attachment hardware from contacting the housing during normal operation.

            - Housing: Cast-ductile iron or welded steel.

            - Elastomeric Material: Molded, oil-resistant rubber, neoprene, or other elastomeric material.

      - OPEN-SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators" Paragraph below and re-edit for each product.

The configuration and materials of open-spring isolators depend on the equipment being supported. It is possible to have more than one type of open-spring isolator on the same Project. Insert drawing designation for each open-spring isolator type required. Use these designations on Drawings to identify each product.

For information on "CADDY’s CSBOSM Spring Mounts," see http://www.vimco.biz/filecabinet/vimco/Literature/S-2055-01.pdf.

        - Freestanding, Laterally Stable, Open-Spring Isolators: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBOSM Open-Spring Isolators or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

          - Minimum Additional Travel: 50 percent of the required deflection at rated load.

          - Lateral Stiffness: More than 80 percent of rated vertical stiffness.

          - Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

          - Baseplates: Factory-drilled steel plate for bolting to structure with an elastomeric isolator pad attached to the underside. Baseplates shall limit floor load to 500 psig (3447 kPa).

          - Top Plate and Adjustment Bolt: Threaded top plate with adjustment bolt and cap screw to fasten and level equipment.

      - HOUSED-SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators in Two-Part Telescoping Housing" Paragraph below and re-edit for each product.

The configuration and materials of housed-spring isolators depend on the equipment being supported. It is possible to have more than one type of housed-spring isolator on the same Project. Insert drawing designation for each housed-spring isolator type required. Use these designations on Drawings to identify each product.

For information on CADDY’s "CSBSSM Spring Mounts," see http://www.vimco.biz/filecabinet/vimco/Literature/S-3100-01.pdf.

        - Freestanding, Laterally Stable, Open-Spring Isolators in Two-Part Telescoping Housing: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBSSM Housed-Spring Isolators or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

          - Minimum Additional Travel: 50 percent of the required deflection at rated load.

          - Lateral Stiffness: More than 80 percent of rated vertical stiffness.

          - Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

          - Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators.

            - Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

            - Top housing with [attachment and leveling bolt] [threaded mounting holes and internal leveling device] [elastomeric pad].

      - SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators with Vertical-Limit Stop Restraint" Paragraph below and re-edit for each product.

The configuration and materials of restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of restrained-spring isolator on the same Project. Insert drawing designation for each restrained-spring isolator type required. Use these designations on Drawings to identify each product.

For information on CADDY’s "CSBOSM Spring Mountss," see http://www.vimco.biz/filecabinet/vimco/Literature/S-2030-01.

        - Freestanding, Laterally Stable, Open-Spring Isolators with Vertical-Limit Stop Restraint: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBOSM Spring Isolators or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Housing: Steel housing with vertical-limit stops to prevent spring extension due to weight being removed.

            - Base with holes for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

            - Top plate with [threaded mounting holes] [elastomeric pad].

            - Internal leveling bolt that acts as blocking during installation.

          - Restraint: Limit stop as required for equipment and authorities having jurisdiction.

          - Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

          - Minimum Additional Travel: 50 percent of the required deflection at rated load.

          - Lateral Stiffness: More than 80 percent of rated vertical stiffness.

          - Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

      - HOUSED-RESTRAINED-SPRING ISOLATORS

Copy "Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing" Paragraph below and re-edit for each product.

The configuration and materials of housed-restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of housed-restrained-spring isolator on the same Project. Insert drawing designation for each housed-restrained-spring isolator type required. Use these designations on Drawings to identify each product.

For information on CADDY’s "CSBRSM Spring Mounts," see http://www.vimco.biz/filecabinet/vimco/Literature/S-2075-01.pdf.

        - Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBRSM Housed-Restrained-Spring Isolators or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators. Housings are equipped with [adjustable] [non-adjustable] snubbers to limit vertical movement.

            - Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

            - Threaded top housing with adjustment bolt and cap screw to fasten and level equipment.

          - Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

          - Minimum Additional Travel: 50 percent of the required deflection at rated load.

          - Lateral Stiffness: More than 80 percent of rated vertical stiffness.

          - Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

      - PIPE-RISER RESILIENT SUPPORT

Copy "Description" Paragraph below and re-edit for each product.

The configuration and materials of pipe-riser resilient supports depend on the equipment being supported. It is possible to have more than one type of pipe-riser resilient support on the same Project. Insert drawing designation for each pipe-riser resilient support type required. Use these designations on Drawings to identify each product.

For information on CADDY’s pipe riser resilient supports, see http://www.vimco.biz/products.ivnu.

        - Description: All-directional, acoustical pipe anchor consisting of two steel tubes separated by a minimum 1/2-inch- (13-mm-) thick neoprene <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY Pipe-Riser Resilient Support or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Vertical-Limit Stops: Steel and neoprene vertical-limit stops arranged to prevent vertical travel in both directions.

          - Maximum Load Per Support: 500 psig (3.45 MPa) on isolation material providing equal isolation in all directions.

      - RESILIENT PIPE GUIDES

Copy "Description" Paragraph below and re-edit for each product.

The configuration and materials of resilient pipe guides depend on the equipment being supported. It is possible to have more than one type of resilient pipe guide on the same Project. Insert drawing designation for each resilient pipe guide type required. Use these designations on Drawings to identify each product.

For information on CADDY’s resilient pipe guides, see http://www.vimco.biz/products.ivnu.

        - Description: Telescopic arrangement of two steel tubes or post and sleeve arrangement separated by a minimum 1/2-inch- (13-mm-) thick neoprene <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY Resilient Pipe Guides or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

Retain "Factory-Set Height Guide with Shear Pin" Subparagraph below where vertical motion due to pipe expansion and contraction is required and clearances are not readily visible.

          - Factory-Set Height Guide with Shear Pin: Shear pin shall be removable and reinsertable to allow for selection of pipe movement. Guides shall be capable of motion to meet location requirements.

      - AIR-SPRING ISOLATORS

Copy "Freestanding, Single or Multiple, Compressed-Air Bellows" Paragraph below and re-edit for each product.

The configuration and materials of air-spring isolators depend on the equipment being supported. It is possible to have more than one type of air-spring isolator on the same Project. Insert drawing designation for each air-spring isolator type required. Use these designations on Drawings to identify each product.

For information on CADDY’s "CSBAS Air Spring Isolators," see http://www.vimco.biz/filecabinet/vimco/Literature/S-2900-01.pdf.

        - Freestanding, Single or Multiple, Compressed-Air Bellows: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBAS Air-Spring Isolators or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Bellows Assembly: Upper and lower powder-coated steel sections connected by a replaceable, flexible, nylon-reinforced neoprene bellows or similar elastomeric material.

          - Maximum Natural Frequency: 3 Hz.

          - Operating Pressure Range: 25 to 100 psig (172 to 690 kPa).

          - Burst Pressure: At least three times manufacturer's published maximum operating pressure.

Retain subparagraph below if air springs are mounted independent of each other and are not supplied by a constant pressure-regulated air supply.

          - Tank valves.

      - RESTRAINED-AIR-SPRING ISOLATORS

Copy "Freestanding, Single or Multiple, Compressed-Air Bellows with Vertical-Limit Stop Restraint" Paragraph below and re-edit for each product.

The configuration and materials of restrained-air-spring isolators depend on the equipment being supported. It is possible to have more than one type of restrained-air-spring isolator on the same Project. Insert drawing designation for each restrained-air-spring isolator type required. Use these designations on Drawings to identify each product.

For information on CADDY’s "CSBASR Restrained Air Spring Isolators," see http://www.vimco.biz/filecabinet/vimco/Literature/S-2900-02.pdf.

        - Freestanding, Single or Multiple, Compressed-Air Bellows with Vertical-Limit Stop Restraint: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBASR Restrained-Air-Spring Isolators or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Housing: Steel housing with vertical-limit stops to prevent spring extension due to weight being removed.

            - Base with holes for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

            - Top plate with [threaded mounting holes] [elastomeric pad].

            - Internal leveling bolt that acts as blocking during installation.

          - Restraint: Limit stop as required for equipment and authorities having jurisdiction.

          - Minimum Additional Travel: 50 percent of the required deflection at rated load.

          - Lateral Stiffness: More than 80 percent of rated vertical stiffness.

          - Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

          - Bellows Assembly: Upper and lower powder-coated steel sections connected by a replaceable, flexible, nylon-reinforced neoprene bellows or similar elastomeric material.

          - Maximum Natural Frequency: [3 Hz] <Insert frequency>.

          - Operating Pressure Range: 25 to 100 psig (172 to 690 kPa).

          - Burst Pressure: At least three times manufacturer's published maximum operating pressure.

Retain subparagraph below if air springs are mounted independent of each other and are not supplied by a constant pressure-regulated air supply.

          - Tank valves.

      - ELASTOMERIC HANGERS

Copy "Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric hangers depend on the equipment being supported. It is possible to have more than one type of elastomeric hanger on the same Project. Insert drawing designation for each elastomeric hanger type required. Use these designations on Drawings to identify each product.

For information on CADDY’s "CSBRH Spring and Rubber Hangers," see http://www.vimco.biz/filecabinet/vimco/Literature/S-2300-01.pdf.

        - Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBRH Elastomeric Mounts or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Frame: Steel, fabricated with a connection for an upper threaded hanger rod and an opening on the underside to allow for a maximum of 30 degrees of angular lower hanger-rod misalignment without binding or reducing isolation efficiency.

          - Dampening Element: Molded, oil-resistant rubber, neoprene, or other elastomeric material with a projecting bushing for the underside opening preventing steel to steel contact.

      - SPRING HANGERS

Copy "Combination Coil-Spring and Elastomeric-Insert Hanger with Spring and Insert in Compression" Paragraph below and re-edit for each product.

The configuration and materials of spring hangers depend on the equipment being supported. It is possible to have more than one type of spring hanger on the same Project. Insert drawing designation for each spring hanger type required. Use these designations on Drawings to identify each product.

For information on CADDY’s "CSBSRH Spring and Rubber Hangers," see http://www.vimco.biz/filecabinet/vimco/Literature/S-2400-01.pdf.

        - Combination Coil-Spring and Elastomeric-Insert Hanger with Spring and Insert in Compression: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBSRH Spring Hangers or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Frame: Steel, fabricated for connection to threaded hanger rods and to allow for a maximum of 30 degrees of angular hanger-rod misalignment without binding or reducing isolation efficiency.

          - Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

          - Minimum Additional Travel: 50 percent of the required deflection at rated load.

          - Lateral Stiffness: More than 80 percent of rated vertical stiffness.

          - Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

          - Elastomeric Element: Molded, oil-resistant rubber or neoprene. Steel-washer-reinforced cup to support spring and bushing projecting through bottom of frame.

Retain "Adjustable Vertical Stop" Subparagraph below if a vertical-limit stop is required.

          - Adjustable Vertical Stop: Steel washer with neoprene washer "up-stop" on lower threaded rod.

          - Self-centering hanger-rod cap to ensure concentricity between hanger rod and support spring coil.

      - SNUBBERS

For information on CADDY’s "CSBSNB Seismic Snubbers," see http://www.vimco.biz/filecabinet/vimco/Literature/S-3100-51.pdf.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBSNB Snubbers or comparable product by one of the following:

          - Vibration Management Corp.

          - Vibration Mountings & Controls, Inc.

          - <Insert manufacturer's name>.

        - Description: Factory fabricated using welded structural-steel shapes and plates, anchor bolts, and replaceable resilient isolation washers and bushings.

          - Resilient Isolation Washers and Bushings: Oil- and water-resistant neoprene.

          - Maximum 1/4-inch (6-mm) air gap, and minimum 1/4-inch- (6-mm-) thick resilient cushion.

Metal framing systems are specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

      - SEISMIC RESTRAINTS – RIGID TYPE

For information on CADDY’s Rigid Seismic Bracing, see https://www.erico.com/category.asp?category=R152.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide <CADDY, a brand of nVent; CADDY Structure Attachments, Sway Brace, and Lateral Telescoping Brace for Rigid Seismic Bracing or comparable product by one of the following:

          - B-line, an Eaton business.

          - Unistrut; Part of Atkore International.

          - <Insert manufacturer's name>.

        - Description: MFMA-4, shop- or field-fabricated bracing assembly made of ANSI/AISI S100 slotted steel channels, ANSI/ASTM A53 steel pipe in accordance with NFPA 13 or other rigid steel brace member with accessories for attachment to braced component at one end and to building structure at the other end and other matching components and with corrosion-resistant coating; rated in tension, compression, and torsion forces.

      - SEISMIC RESTRAINTS - CABLE TYPE

For information on CADDY’s "Seismic Wire Rope/Cable™" bracing, see https://www.erico.com/category.asp?category=R146.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; [Size 12, RED] [Size 18, WHITE] [Size 36, BLUE] [Size 48, YELLOW] Seismic Wire Rope/Cable Bracing or comparable product by one of the following:

          - Loos & Co.

          - Vibration Mountings & Controls, Inc.

          - <Insert manufacturer's name>.

        - Restraint Cables: [ASTM A1023 galvanized-] [ASTM A603 galvanized-] [ASTM A492 stainless ]steel cables. End connections made of steel assemblies with thimbles, brackets, swivel, and bolts designed for seismic restraining cable service; with fittings attached by means of poured socket, swaged socket, or mechanical (Flemish eye) loop.

        - Restraint cable assembly and cable fittings must comply with ASCE/SEI 19. All cable assembly fittings shall maintain the minimum breaking force of the cable. U-shaped cable clips and wedge-type end fittings do not comply and are unacceptable.

      - SEISMIC-RESTRAINT ACCESSORIES

For information on CADDY’s "Seismic Wire Rope/Cable™" Bracing Accessories, see https://www.erico.com/category.asp?category=R146

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; [Size 12, RED] [Size 18, WHITE] [Size 36, BLUE] [Size 48, YELLOW] Seismic Wire Rope/Cable Spools and Oval Sleevesm URC Universal Restraint Clips, NPC No-Pry Clips, Quick Clip, and RS-1 Rod Stiffener Clips, and Structure Attachment and Sway Brace fittings for 1 to 2 inch (25 to 50 mm) brace member or comparable product by one of the following:

          - Vibration Eliminator Co., Inc.

          - Vibration Mountings & Controls, Inc.

          - <Insert manufacturer's name>.

Retain "Hanger-Rod Stiffener" Paragraph below for strengthening resistance of hanger rods against seismic forces that may cause buckling of rods; delete if detailed on Drawings. Use with either channel- or cable-type bracing assemblies when required to counter seismic forces. Detail fabrication and indicate locations on Drawings.

        - Hanger-Rod Stiffener: Steel tube, steel channel-type strut, or steel angle rod stiffener member clamped to hanger rod with rod stiffener clips.

        - Hinged and Swivel Brace Attachments: Multifunctional steel connectors for attaching hangers to [seismic restraints – cable type] [and] [seismic restraints – rigid type] .

        - Bushings for Floor-Mounted Equipment Anchor Bolts: Neoprene bushings designed for rigid equipment mountings, and matched to type and size of anchor bolts and studs.

        - Bushing Assemblies for Wall-Mounted Equipment Anchorage: Assemblies of neoprene elements and steel sleeves designed for rigid equipment mountings, and matched to type and size of attachment devices used.

        - Resilient Isolation Washers and Bushings: One-piece, molded, oil- and water-resistant neoprene, with a flat washer face.

      - POST-INSTALLED CONCRETE ANCHORS IN CONCRETE AND MASONRY

For information on CADDY’s "Post-Installed Concrete Anchors," see https://www.erico.com/category.asp?category=R1250.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY [Wedge Expansion Anchors] [and] [Screw Anchors] or comparable product by one of the following:

          - Powers Fasteners.

          - Simpson Strong-Tie Co., Inc.

          - <Insert manufacturer's name>.

        - Post-Installed Expansion and Undercut Anchors in concrete and masonry to be seismically pre-qualified in accordance with ACI 355.2 testing.

        - Post-Installed Adhesive Anchors in concrete and masonry to be seismically pre-qualified in accordance with ACI 355.4 testing.

        - Post-Installed Anchors in Concrete to be designated in accordance with [ACI 318-08 Appendix D for 2009] [ACI 318-11 Appendix D for 2012 IBC] [ACI 318-14 Chapter 17 for 2015 or 2018 IBC].

        - Post-Installed anchors in masonry to be designed in accordance with TMS 402.

      - CONCRETE INSERTS

For information on CADDY’s "Rod Lock Concrete Inserts," see https://www.erico.com/category.asp?category=R2853.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY Rod Lock Metal Deck and Plywood Form Inserts or comparable product by one of the following:

          - Powers Fasteners.

          - Simpson Strong-Tie Co., Inc.

          - <Insert manufacturer's name>.

        - Preset Concrete Inserts: To be seismically pre-qualified in accordance with ICC-ES AC446.

      - VIBRATION ISOLATION EQUIPMENT BASES

For information on CADDY’s "CSBIB Equipment Bases," see http://www.vimco.biz/filecabinet/vimco/Literature/S-3000-01.pdf,

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBIB Vibration Isolation Equipment Bases or comparable product by one of the following:

          - Vibration Management Corp.

          - Vibration Mountings & Controls, Inc.

          - <Insert manufacturer's name>.

        - Steel Rails: Factory-fabricated, welded, structural-steel rails.

          - Design Requirements: Lowest possible mounting height with not less than 1-inch (25-mm) clearance above the floor. Include equipment anchor bolts and auxiliary motor slide rails.

Retain first subparagraph below if steel rails are required for pumps.

            - Include supports for suction and discharge elbows for pumps.

          - Structural Steel: Steel shapes, plates, and bars complying with ASTM A36/A36M. Rails shall have shape to accommodate supported equipment.

          - Support Brackets: Factory-welded steel brackets on frame for outrigger isolation mountings and to provide for anchor bolts and equipment support.

        - Steel Bases: Factory-fabricated, welded, structural-steel bases and rails.

          - Design Requirements: Lowest possible mounting height with not less than 1-inch (25-mm) clearance above the floor. Include equipment anchor bolts and auxiliary motor slide bases or rails.

Retain first subparagraph below if steel bases are required for pumps.

            - Include supports for suction and discharge elbows for pumps.

          - Structural Steel: Steel shapes, plates, and bars complying with ASTM A36/A36M. Bases shall have shape to accommodate supported equipment.

          - Support Brackets: Factory-welded steel brackets on frame for outrigger isolation mountings and to provide for anchor bolts and equipment support.

        - Concrete Inertia Base: [Factory-fabricated] [or] [field-fabricated], welded, structural-steel bases and rails ready for placement of cast-in-place concrete.

          - Design Requirements: Lowest possible mounting height with not less than 1-inch (25-mm) clearance above the floor. Include equipment anchor bolts and auxiliary motor slide bases or rails.

Retain first subparagraph below if inertia bases are required for pumps.

            - Include supports for suction and discharge elbows for pumps.

          - Structural Steel: Steel shapes, plates, and bars complying with ASTM A36/A36M. Bases shall have shape to accommodate supported equipment.

          - Support Brackets: Factory-welded steel brackets on frame for outrigger isolation mountings and to provide for anchor bolts and equipment support.

          - Fabrication: Fabricate steel templates to hold equipment anchor-bolt sleeves and anchors in place during placement of concrete. Obtain anchor-bolt templates from supported equipment manufacturer.

      - RESTRAINED ISOLATION ROOF-CURB RAILS

For information on CADDY’s "CSBRC Equipment Bases," see http://www.vimco.biz/filecabinet/vimco/Literature/P-3001.pdf.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY CSBRC Restrained Isolation Roof-Curb Rails or comparable product by one of the following:

          - Vibration Management Corp.

          - Vibration Mountings & Controls, Inc.

          - <Insert manufacturer's name>.

        - Description: Factory-assembled, fully enclosed, insulated, air- and watertight curb rail designed to resiliently support equipment and to withstand seismic[ and wind] forces.

        - Upper Frame: The upper frame shall provide continuous support for equipment and shall be captive to resiliently resist seismic[ and wind] forces.

        - Lower Support Assembly: The lower support assembly shall be formed sheet metal section containing adjustable and removable steel springs that support the upper frame. The lower support assembly shall have a means for attaching to building structure and a wood nailer for attaching roof materials, and shall be insulated with a minimum of 2 inches (50 mm) of rigid, glass-fiber insulation on inside of assembly. Adjustable, restrained-spring isolators shall be mounted on elastomeric vibration isolation pads and shall have access ports, for level adjustment, with removable waterproof covers at all isolator locations. Isolators shall be located so they are accessible for adjustment at any time during the life of the installation without interfering with the integrity of the roof.

        - Snubber Bushings: All-directional, elastomeric snubber bushings at least 1/4 inch (6 mm) thick.

        - Water Seal: Galvanized sheet metal with EPDM seals at corners, attached to upper support frame, extending down past wood nailer of lower support assembly, and counterflashed over roof materials.

- EXECUTION

      - EXAMINATION

        - Examine areas and equipment to receive vibration isolation and seismic[- and wind]-control devices for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in of reinforcement and cast-in-place anchors to verify actual locations before installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - APPLICATIONS

        - Multiple Pipe Supports: Secure pipes to trapeze member with clamps approved for application by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

Indicate on Drawings, by details, schedules, or a combination of both, the locations where hanger rods for individual pipes and hanger rods for trapeze hangers require hanger-rod stiffeners.

        - Hanger-Rod Stiffeners: Install hanger-rod stiffeners where indicated or scheduled on Drawings to receive them and where required to prevent buckling of hanger rods due to seismic forces.

        - Strength of Support and Seismic-Restraint Assemblies: Where not indicated, select sizes of components so strength is adequate to carry present and future static and seismic loads within specified loading limits.

      - INSTALLATION OF VIBRATION CONTROL[, WIND LOAD CONTROL,] AND SEISMIC-RESTRAINT DEVICES

        - Provide vibration control devices for systems and equipment where indicated in Equipment Schedules or Vibration Control Devices Schedules, where shown on Drawings, or where Specifications indicate they are to be installed on specific equipment and systems.

        - Provide seismic restraint[ and wind load control] devices for systems and equipment where indicated in Equipment Schedules or Seismic-Restraint Devices Schedules, where shown on Drawings, where Specifications indicate they are to be installed on specific equipment and systems, and where required by applicable codes.

        - Installation of vibration isolators must not cause any change of position of equipment, piping, or ductwork resulting in stresses or misalignment.

        - Comply with requirements in Section 077200 "Roof Accessories" for installation of roof curbs, equipment supports, and roof penetrations.

        - Equipment Restraints:

Indicate type and quantity of snubbers described in first subparagraph below on Drawings or in the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

          - Install seismic snubbers on HVAC equipment mounted on vibration isolators. Locate snubbers as close as possible to vibration isolators and bolt to equipment base and supporting structure.

          - Install resilient bolt isolation washers on equipment anchor bolts where clearance between anchor and adjacent surface exceeds 0.125 inch (3.2 mm).

          - Install seismic-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] that provides required submittals for component.

        - Piping Restraints:

          - Comply with restraint spacing requirements in MSS SP-127.

In first subparagraph below, options for 40 and 80 feet (12 and 24 m) are recommended by MSS SP-127. Revise these dimensions based on the configuration of piping.

          - Space lateral supports a maximum of [40 feet (12 m)] <Insert dimension> o.c., and longitudinal supports a maximum of [80 feet (24 m)] <Insert dimension> o.c.

          - Brace a change of direction longer than 12 feet (3.7 m).

        - Install cables so they do not bend across edges of adjacent equipment or building structure.

        - Install seismic-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] that provides required submittals for component.

        - Install bushing assemblies for anchor bolts for floor-mounted equipment, arranged to provide resilient media between anchor bolt and mounting hole in concrete base.

        - Install bushing assemblies for mounting bolts for wall-mounted equipment, arranged to provide resilient media where equipment or equipment-mounting channels are attached to wall.

        - Attachment to Structure: If specific attachment is not indicated, anchor bracing to structure at flanges of beams, at upper truss chords of bar joists, or at concrete members.

        - Mechanical Anchor Bolts:

          - Identify position of reinforcing steel and other embedded items prior to drilling holes for anchors. Do not damage existing reinforcing or embedded items during coring or drilling. Notify the structural engineer if reinforcing steel or other embedded items are encountered during drilling. Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

          - Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

          - Wedge-Type Anchor Bolts: Protect threads from damage during anchor installation. Heavy-duty sleeve anchors shall be installed with sleeve fully engaged in the structural element to which anchor is to be fastened.

          - Adhesive-Type Anchor Bolts: Clean holes to remove loose material and drilling dust prior to installation of adhesive. Place adhesive in holes proceeding from the bottom of the hole and progressing toward the surface in such a manner as to avoid introduction of air pockets in the adhesive.

          - Set anchors to manufacturer's recommended torque, using a torque wrench.

          - Install zinc-coated steel anchors for interior and stainless steel anchors for exterior applications.

      - ACCOMMODATION OF DIFFERENTIAL SEISMIC MOTION

Coordinate this article with Drawings.

        - Flexibility for Differential Movement: HVACR components shall be provided with adequate flexibility to accommodate differential movement between portions of the structure that move differentially, as determined in accordance with ASCE 7.

      - FIELD QUALITY CONTROL

Retain "Testing Agency" and "Perform tests and inspections" paragraphs below to identify who shall perform tests and inspections. If retaining second option in "Testing Agency" Paragraph, or if retaining "Perform tests and inspections" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

        - Manufacturer’s Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

        - Tests and Inspections:

          - Perform tests and inspections[ with assistance of a factory-authorized service representative].

          - Provide evidence of recent calibration of test equipment by a testing agency acceptable to authorities having jurisdiction.

          - Schedule test with Owner, through Architect, before connecting anchorage device to restrained component (unless postconnection testing has been approved), and with at least seven days' advance notice.

          - Obtain Architect's approval before transmitting test loads to structure. Provide temporary load-spreading members.

          - Test at least [four] <Insert number> of each type and size of installed anchors and fasteners selected by Architect.

          - Test to 90 percent of rated proof load of device.

          - Measure isolator restraint clearance.

          - Measure isolator deflection.

          - Verify snubber minimum clearances.

Retain subparagraph below if restrained-air-spring isolators are included in Project.

          - Test and adjust restrained-air-spring isolator controls and safeties.

        - Remove and replace malfunctioning units and retest as specified above.

        - Prepare test and inspection reports.

      - ADJUSTING

        - Adjust isolators after piping is at operating weight.

        - Adjust limit stops on restrained-spring isolators to mount equipment at normal operating height. After equipment installation is complete, adjust limit stops so they are out of contact during normal operation.

      - INSTALLATION OF AIR-SPRING ISOLATORS

Retain "Independent Isolator Installation" Paragraph below if air springs are mounted independent of each other and are not supplied by a constant pressure-regulated air supply.

        - Independent Isolator Installation:

          - Install tank valve into each air isolator.

          - Inflate each isolator to [height] [and] [pressure] specified on Drawings.

Retain "Pressure-Regulated Isolator Installation" Paragraph below if air springs are supplied with a constant pressure-regulated air supply.

        - Pressure-Regulated Isolator Installation:

          - Coordinate the constant pressure-regulated air supply to air springs with the requirements for piping and connections specified in Section 221513 "General-Service Compressed-Air Piping."

          - Connect all pressure regulators to a single dry, filtered [facility] [constant] air supply.

          - Inflate isolators to [height] [and] [or] [pressure] specified on Drawings.

      - INSTALLATION OF VIBRATION ISOLATION EQUIPMENT BASES

        - Coordinate the location of embedded connection hardware with supported equipment attachment and mounting points and with requirements for concrete reinforcement and formwork specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053, "Miscellaneous Cast-in-Place Concrete."]

        - Coordinate dimensions of equipment bases with requirements of isolated equipment specified in this and other Sections. Where dimensions of base are shown on Drawings, they may require adjustment to accommodate isolated equipment.

END OF SECTION 230548