Copyright 2016 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to CADDY, a brand of nVent ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact nVent, 31700 Solon Road, Solon, OH 44139; Phone: (800) 753-9221 | (440) 248-0100; Fax: (440) 848-8405; Website: www.nvent.com; Email: Daniel.Duggan@nVent.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit www.masterspec.com.

SECTION 260548.16 - SEISMIC CONTROLS FOR ELECTRICAL SYSTEMS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Elastomeric isolation pads.

          - Housed-spring isolators.

          - Restrained-spring isolators.

          - Seismic restraint – rigid type.

          - Seismic restraint – cable type.

          - Seismic-restraint accessories.

          - Post-installed concrete anchors.

          - Concrete inserts.

        - Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 260529 "Hangers and Supports for Electrical Systems" for commonly used electrical supports and installation requirements.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - Designated Seismic System: An electrical component that requires design in accordance with ASCE 7, Ch. 13 and for which the Component Importance Factor is greater than 1.00.

        - IBC: International Building Code.

        - IMC: International Mechanical Code.

        - NRTL: Nationally recognized testing agency.

The OPA program has been discontinued and replaced by OPM, but existing OPA numbers can be used for projects based on the code cycle under which OPAs were approved.

        - OPA: OSHPD Preapproval of anchorage number, Office of Statewide Health Planning & Development (for the State of California owned and regulated medical facilities).

        - OPM: Manufacturer's Preapproval Certification Number (for the State of California owned and regulated medical facilities).

        - OSHPD: Office of Statewide Health Planning and Development (for the State of California owned and regulated medical facilities).

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include rated load, rated deflection, and overload capacity for each vibration isolation device.

          - Include load rating for each seismic-restraint fitting or assembly and prying factor for each seismic-restraint structure attachment fitting.

          - Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of vibration isolation device and seismic-restraint component required.

See the Evaluations for a discussion on seismic-restraint capacities and rating services.

            - Tabulate types and sizes of seismic restraints and accessories, complete with listing markings or report numbers and load rating in tension and compression as evaluated by [ICC-ES Product Listing] [UL Product Listing] [FM Approvals] [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

            - Annotate to indicate application of each product submitted and compliance with requirements.

          - Interlocking Snubbers: Include ratings for horizontal, vertical, and combined loads.

        - Shop Drawings:

          - Detail fabrication and assembly of equipment bases. Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting.

            - Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting.

Retain "Delegated Design Submittal" Paragraph below if design services have been delegated to Contractor.

        - Delegated Design Submittal: For each vibration isolation[, and] seismic-restraint[, and wind-force] device that is required by this Section or is indicated in the Contract Documents, submit the following:

          - Design Calculations: Calculate static or dynamic loading as required by ASCE/SEI 7 due to equipment weight, operation, and seismic[, and wind] forces required for selection of vibration isolators and seismic[, and wind] restraints, and for design of vibration isolation bases.

            - Coordinate design calculations with wind-load calculations required for equipment mounted outdoors. Comply with requirements in other Sections for equipment mounted outdoors.

            - All calculations are to be performed using methods defined in [ASCE/SEI 7-05 for 2009 IBC] [ASCE/SEI 7-10 including Supplement No. 1 for 2012 IBC] [ASCE/SEI 7-10 including Supplement No. 1 for 2015 IBC] [ASCE/SEI 7-16 for 2018 IBC] <Insert ASCE/SEI 7 edition> or as required by authorities having jurisdiction.

          - Vibration Isolator, Seismic[, and Wind Load] Restraint, and Vibration Isolation Base Selection: Select vibration isolators, seismic[, and wind-load] restraints, and vibration isolation bases complying with performance requirements, design criteria, and analysis data.

          - Riser Supports: Include riser diagrams and calculations showing anticipated expansion and contraction at each support point, initial and final loads on building structure, spring deflection changes, and seismic loads. Include certification that riser system was examined for excessive stress and that none exists.

          - All delegated design submittals are to be signed and sealed by the qualified professional engineer responsible for their preparation.

Retain "Seismic Design Calculations" Paragraph below if design services have been delegated to Contractor.

        - Seismic Design Calculations:

ASCE/SEI 7 is generally applicable in most locations, but it is the electrical; engineer's responsibility to determine the applicable building codes and editions thereof, and applicable seismic design standards that apply to this Project. Data and information required for seismic calculations in ASCE/SEI 7 are listed below. ASCE/SEI 7-05, ASCE/SEI 7-10, and ASCE/SEI 7-16 differ somewhat; material from all three editions has been included below and has been noted. The Electrical engineer must delete all inappropriate editions throughout the Section.

          - Calculations must be performed to obtain force information necessary to properly select seismic-restraint devices, fasteners, and anchorage. Calculations are to be performed using methods acceptable to IBC and as presented in the applicable edition of [ASCE 7-05] [ASCE/SEI 7-10] [ASCE/SEI 7-16] [or as otherwise acceptable to authorities having jurisdiction]. Data indicated below, which are specific to individual pieces of equipment, must be obtained by Contractor and must be included in individual component submittal packages.

Data values identified below as applying to all components on Project are to be inserted by the electrical engineer into these specifications where indicated in the following list. Data values, which are specific to an individual generic component and are indicated to be scheduled should be included by the electrical engineer on the Electrical Vibration-Control and Seismic Restraint Device Schedule or the individual component schedules on Drawings. Data values, which are specific to an individual piece of equipment as provided by Contractor and are indicated to be obtained by Contractor must, be included in individual component submittal packages.

Retain first subparagraph below if ASCE/SEI 7-16 applies to this Project.

          - The following calculation factors refer to ASCE/SEI 7-16, Ch. 13, "Seismic Design Requirements for Nonstructural Components." All Section, Paragraph, Equation, and Table numbers refer to ASCE/SEI 7-16 unless otherwise indicated.

            - Horizontal Seismic Design Force Fp is calculated by Eq. 13.3-1. Factors below must be obtained for this calculation:

              - SDS = Spectral Acceleration: <Insert value>. (Value applies to all components on the Project. Value is obtained by electrical engineer from project structural engineer, Section 11.4.5.)

              - ap = Component Amplification Factor: <Insert value>. Schedule for each component. (Varies from 1.00 to 2.50. Selected by electrical engineer from Table 13.6-1.)

              - Ip = Component Importance Factor: Schedule for each component. Value [1.00] [1.50] assigned by electrical engineer as explained in Editing Instruction document and in Section 13.1.3 (Value 1.00 or 1.50).

              - Wp = Component Operating Weight: Obtained by Contractor from each component submittal.

              - Rp = Component Response Modification Factor: Schedule for each component. (Varies from 1.00 to 12. Selected by electrical engineer from Table 13.6-1.)

              - z = Height in structure of point of attachment of component for the base. Determined from Project Drawings for each component by Contractor. For items at or below the base, "z" shall be taken as zero.

              - h = Average roof height of structure for the base. Determined from Project Drawings for each component by Contractor.

            - In lieu of seismic design forces, dynamic analysis may be used as defined in Para. 13.3.1.4 where applicable and approved by authorities having jurisdiction.

            - Seismic Relative Displacement Dpl is calculated using methods explained in Para. 13.3.2. Factors below must be obtained for this calculation.

              - Dp = Relative seismic displacement that the component must be designed to accommodate - calculated in accordance with Para. 13.3.2.

              - Ie = Structure Importance Factor: <Insert value>. Value applies to all components on Project. Value is obtained by electrical engineer from Project structural engineer, Section 11.5.1.

              - δxA = Deflection at Building Level x of Structure A: Schedule for each component. Value is determined in accordance with Eq. 12.8-15 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

              - δyA = Deflection at Building Level y of Structure A: Schedule for each component. Value is determined by electrical engineer from Project structural engineer in accordance with Eq. 12.8-15 and depends upon location of component in the building.

              - δyB = Deflection at Building Level y of Structure B: Schedule for each component. Value is determined in accordance with Eq. 12.8-15 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

              - hx = Height of Level x to which Upper Connection Point Is Attached: Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - hy = Height of Level y to which Upper Connection Point Is Attached:  Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - ΔaA = Allowable Story Drift for Structure A: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

              - ΔaB = Allowable Story Drift for Structure B: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

              - hsx = Story Height Used in the Definition of the Allowable Drift Δa: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

            - Component Period Dpl is calculated using methods explained in Para. 13.3.3. Factors below must be obtained for this calculation:

              - Tp = Component Fundamental Period: Determined by Contractor from Project Drawings and manufacturer's data.

              - Wp = Component Operating Weight: Determined by Contractor from Project Drawings and manufacturer's data.

              - g = Gravitational Acceleration: [32.17 ft./sec2 (9.81 m/sec2)] <Insert ft./sec2 (m/sec2)>.

              - Kp = Combined Stiffness of the Component, Supports, and Attachments: Determined by Delegated Design seismic engineer.

Retain first subparagraph below if ASCE/SEI 7-10 applies to this Project.

          - The following calculation factors refer to ASCE/SEI 7-10, Ch. 13, "Seismic Design Requirements for Nonstructural Components." All Section, Paragraph, Equation, and Table numbers refer to ASCE/SEI 7-10 unless otherwise indicated.

            - Horizontal Seismic Design Force Fp is calculated by Eq. 13.3-1. Factors below must be obtained for this calculation.

              - SDS = Spectral Acceleration: <Insert value> Value applies to all components on Project. Value is obtained by electrical engineer from Project structural engineer, Section 11.4.5.

              - ap = Component Amplification Factor: Schedule for each component. Varies from 1.00 to 2.50. Selected by electrical engineer from Table 13.6-1.

              - Ip = Component Importance Factor: Schedule for each component. Value [1.00] [1.50] assigned by electrical engineer as explained in Editing Instruction document and in Section 13.1.3 (Value 1.00 or 1.50).

              - Wp = Component Operating Weight Obtained by Contractor for each component from equipment submittal.

              - Rp = Component Response Modification Factor: Schedule for each component. Varies from 1.00 to 12. Selected by electrical engineer from Table 13.6-1.

              - z = Height in structure of point of attachment of component for the base. Determined from Project Drawings for each component by Contractor. For items at or below the base, "z" shall be taken as 0.

              - h = Average roof height of structure for the base. Determined from Project Drawings for each component by Contractor.

            - In lieu of seismic design forces, accelerations may be determined by the modal analysis procedures of Section 12.9 as defined in Para. 13.3.1 where applicable and approved by authorities having jurisdiction.

            - Seismic Relative Displacement Dpl is calculated using methods explained in Para. 13.3.2.  Factors below must be obtained for this calculation.

              - Dp = Relative seismic displacement that the component must be designed to accommodate - calculated in accordance with Para. 13.3.2.

              - Ie = Structure Importance Factor: <Insert value> Value applies to all components on Project. Value is obtained by electrical engineer from Project structural engineer, Secion 11.5.1.

              - δxA = Deflection at Building Level x of Structure A: Schedule for each component. Value is determined in accordance with Eq. 12.8-15 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

              - δyA = Deflection at Building Level y of Structure A: Schedule for each component. Value is determined in accordance with Eq. 12.8-15 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer, Section 11.4.5.

              - δyB = Deflection at Building Level y of Structure B: Schedule for each component. Value is determined in accordance with Eq. 12.8-15 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer, Section 11.4.5.

              - hx = Height of Level x to which Upper Connection Point Is Attached:  Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - hy = Height of Level y to which Upper Connection Point Is Attached: Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - ΔaA = Allowable Story Drift for Structure A: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer, Section 11.4.5.

              - ΔaB = Allowable Story Drift for Structure B: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer, Section 11.4.5.

              - hsx = Story Height Used in the definition of the Allowable Drift Δa: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer, Section 11.4.5.

Retain subparagraph below if ASCE 7-05 applies to this Project.

          - The following calculation factors refer to ASCE 7-05, Ch. 13, "Seismic Design Requirements for Nonstructural Components." All Section, Paragraph, Equation, and Table numbers refer to ASCE 7-05 unless otherwise indicated.

            - Horizontal Seismic Design Force Fp is calculated by Eq. 13.3-1. Factors below must be obtained for this calculation:

              - SDS = Spectral Acceleration: <Insert value> Value applies to all components on Project. Value is obtained by electrical engineer from Project structural engineer, Section 11.4.4.

              - ap = Component Amplification Factor: Schedule for each component. Varies from 1.00 to 2.50. Selected by electrical engineer from Table 13.6-1.

              - Ip = Component Importance factor: Schedule for each component. Value [1.00] [1.50] assigned by electrical engineer as explained in Editing Instructions document and in Section 13.1.3 (Value 1.00 or 1.50).

              - Wp = Component Operating Weight: Obtained by Contractor from each component submittal.

              - Rp = Component Response Modification Factor: Schedule for each component. Varies from 1.00 to 12. Selected by electrical engineer from Table 13.6-1.

              - z = Height in structure of point of attachment of component for the base. Determined from Project Drawings for each component by Contractor. For items at or below the base, "z" shall be taken as zero.

              - h = Average roof height of structure for the base. Determined from Project Drawings by Contractor.

            - Alternate calculation method with Eq. 13.3-4 may be used as indicated in Section 13.3.1 where applicable and approved by authorities having jurisdiction.

            - Seismic Relative Displacement Dp is calculated using methods explained in Para. 13.3.2. Factors below must be obtained for this calculation.

              - δxA = Deflection at Building Level x of Structure A: Schedule for each component. Value is determined as defined in Section 12.8.6 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

              - δyA = Deflection at Building Level y of Structure A: Schedule for each component. Value is determined as defined in Section 12.8.6 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

              - δyB = Deflection at Building Level y of Structure B: Schedule for each component. Value is determined as defined in Section 12.8.6 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

              - hx = Height of Level x to which Upper Connection Point Is Attached: Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - hy = Height of Level y to which Upper Connection Point Is Attached: Determined for each component by Contractor from Project Drawings and manufacturer's data.

              - ΔaA = Allowable Story Drift for Structure A: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

              - ΔaB = Allowable Story Drift for Structure B: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

              - hsx = Story Height Used in the Definition of the Allowable Drift Δa: Schedule for each component. Value is determined in accordance with Eq. 12.12-1 and depends upon location of component in the building. Value is obtained by electrical engineer from Project structural engineer.

        - Wind-Load Design Calculations

ASCE/SEI 7 is generally applicable in most locations, but it is the electrical engineer's responsibility to determine the applicable building codes and editions thereof, and applicable seismic design standards that apply to this Project. Data and information required for seismic calculations in ASCE/SEI 7 are listed below. ASCE/SEI 7-05, ASCE/SEI 7-10, and ASCE/SEI 7-16 differ somewhat; material from all three editions has been included below and has been noted. The electrical engineer must delete all inappropriate editions throughout the Section.

          - Calculations must be performed to obtain force information necessary to properly select wind-load-restraint devices, fasteners, and anchorage. Calculations are to be performed using methods acceptable to the IBC and as presented in the applicable edition of [ASCE/SEI 7-05] [ASCE/SEI 7-10] [ASCE/SEI 7-16] [or as otherwise acceptable to authorities having jurisdiction]. Data indicated below, which is specific to individual pieces of equipment must be obtained by Contractor and must be included in individual component submittal packages.

Data values identified below as applying to all components on Project are to be inserted, by the electrical engineer, in these Specifications where indicated in the following list. Data values, which are specific to an individual generic component and are indicated to be scheduled, should be included by the electrical engineer on the Electrical Vibration-Control and Seismic Restraint Device Schedule or the individual component schedules on Drawings. Data values, which are specific to an individual piece of equipment as provided by Contractor and are indicated to be obtained by Contractor, must be included in individual component submittal packages.

Retain first following subparagraph below if ASCE/SEI 7-16 applies to this Project.

            - The following calculation factors refer to ASCE/SEI 7-16, Ch. 26 Wind Loads: General Requirements"; Ch. 29 Wind Loads on Building Appurtenances"; and Ch. 30 "Wind Loads: Components and Cladding. " All Section, Paragraph, Equation, and Table numbers refer to ASCE/SEI 7-16 unless otherwise indicated.

Retain first subparagraph below if ASCE/SEI 7-10 applies to this Project.

            - The following calculation factors refer to ASCE/SEI 7-10, Ch. 26 "Wind Loads: General Requirements"; Ch. 29 "Wind Loads on Other Structures and Building Appurtenances"; and Ch. 30 "Wind Loads - Components and Cladding (C & C)." The factors and calculation methods for rooftop equipment on buildings not over 60 ft. (18.3 m) are the same as those in ASCE/SEI 7-16. ASCE/ASI 7-10 does not provide any standards for buildings over 60 ft. (18.3 m). Wind-load designer must use calculation methods acceptable to authorities having jurisdiction.

Retain first subparagraph below if either ASCE/SEI 7-16 or ASCE/SEI 7-10 applies to this Project.

            - Horizontal Design Wind Load Fh and Vertical Wind Uplift Force Fv for rooftop equipment are calculated by Eq. 9.4-2. Factors below must be obtained for this calculation.

              - Risk Category: [I] [II] [III] [IV]. Value applies to all rooftop equipment on building - obtained by electrical engineer from Architect as explained in Section 1.5 and Table 1.5-1.

              - V = Basic Wind Speed: <Insert value> from Wind Hazard map in ASCE/SEI 7 or other approved source.

              - Kd = Wind Directionality Factor: <Insert factor> Value is obtained by electrical engineer from Section 26.6 and Table 26.6-1.

              - Exposure Category: [B] [C] [D] from Sec. 26.7. Value is obtained by electrical engineer.

              - Kzt = Topographic Factor: <Insert factor>. Value is obtained by electrical engineer from Section 26.8 and Table 26.8-1.

              - Ke = Ground Elevation Factor: <Insert factor>. Value is obtained by electrical engineer from Section 26.8 and Table 26.8-1.

              - Enclosure Classification: <Insert classification>. Value is obtained by electrical engineer from Section 26.12.

              - GCpi = Internal Pressure Coefficient: <Insert coefficient>. Value obtained by electrical engineer from Table 26.13-1.

              - Kz = Velocity Pressure Exposure Coefficient: <Insert coefficient> Value is obtained by electrical engineer from Section 26.10.1.

              - Kh = Velocity Pressure Exposure Coefficient: <Insert coefficient>. Value obtained by electrical engineer from Section 26.10.1.

              - qz = Velocity Pressure: <Insert lb/sq. ft. (N/sq. m)>. Value is calculated by delegated wind-load design Contractor.

              - qh = Velocity Pressure: <Insert lb/sq. ft. (N/sq. m)>. Value is calculated by delegated wind-load design Contractor.

              - GCr = Gust Factor for Roof-Mounted Equipment: <Insert factor>. Value is obtained by electrical engineer from Section 29.4.1.

              - Af = Vertical projected area of rooftop equipment on a plane normal to the direction of wind <Insert sq. ft. (sq. m)>. Value is obtained by Contractor from equipment manufacturer.

              - Ar = Horizontal projected area of rooftop equipment <Insert sq. ft. (sq. m)>. Value is obtained by Contractor from equipment manufacturer.

            - Design Wind Pressure "p" for external sidewall-mounted equipment such as louvers is calculated using the methods in ASCE/SEI 7-16, Ch. 30. The methods differ for low-rise, mid-rise <60 ft. (h <18.3 m), and high-rise 60 ft. <h <160 ft. (18.3 m < h <48.8 m). Within each height category, calculation methods also differ because of building shape and other factors. The required calculation factors and equations are found in Chapter 30.

Retain the first subparagraph below if ASCE 7-05 applies to this Project.

          - The following calculation factors refer to ASCE 7-05, Ch. 6 "Wind Loads." All Section, Paragraph, Equation, and Table numbers refer to ASCE 7-05 unless otherwise indicated.

            - F = Design wind load for rooftop equipment. Calculated by delegated wind-load design Contractor using methods presented in ASCE 7-05, Ch. 6.

            - qz = Velocity pressure is calculated by delegated wind load design Contractor.

            - G = Gust Effect Factor: 0.85. Value is obtained by electrical engineer - value may be calculated as presented in Para. 6.5.8.

            - Cf = Force Coefficient: <Insert factor>. Value obtained by electrical engineer from Figure 6-20.

            - Af = Projected area normal to the wind [except when Cf is adjusted for actual surface area sq. ft. (sq. m)]: Value is calculated by delegated wind-load design Contractor using wind data found in ASCE 7-05 and equipment dimension data supplied by equipment manufacturer.

Retain "Seismic(- and Wind)-Restraint Details" Subparagraph below only if seismic design requirements apply but calculations have not been made and details or charts on Drawings do not describe seismic or wind restraints in detail. Retaining subparagraph will require Contractor to submit seismic-restraint Shop Drawings prepared by a professional engineer. Revise to suit local requirements.

          - Seismic[- and Wind]-Restraint Details:

            - Design Analysis: To support selection and arrangement of seismic[ and wind] restraints. Include calculations of combined tensile and shear loads.

            - Details: Indicate fabrication and arrangement. Detail attachments of restraints to the restrained items and to the structure. Show attachment locations, methods, and spacings. Identify components, list their strengths, and indicate directions and values of forces transmitted to the structure during seismic events. Indicate association with vibration isolation devices.

Retain first subparagraph below if Project includes equipment mounted outdoors, or otherwise subject to wind loading.

            - Coordinate seismic-restraint and vibration isolation details with wind-restraint details required for equipment mounted outdoors. Comply with requirements in other Sections for equipment mounted outdoors.

            - Product Listing, Preapproval, and Evaluation Documentation: By [an evaluation service member of ICC-ES] [FM Approvals] [OSHPD] [UL] [an agency acceptable to authorities having jurisdiction], showing maximum ratings of restraint items and the basis for approval (tests or calculations).

      - INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

        - Coordination Drawings: Show coordination of vibration isolation device installation and seismic bracing for electrical piping and equipment with other systems and equipment in the vicinity, including other supports and restraints, if any. Electrical components include:

          - Control[ and monitoring] panels.

          - Generators.

          - Luminaires.

          - Motor control centers.

          - Panelboards.

          - Photovoltaic system components.

          - Substations.

          - Switchboards.

          - Switchgear.

          - Transformers.

          - Unit substations.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For [professional engineer] [and] [testing agency].

Retain "Welding certificates" Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Assurance" Article.

        - Welding certificates.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

Include "Special Certification of Designated Seismic Systems" Paragraph below in all Specification Sections that specify Designated Seismic Systems, or as required by authorities having jurisdiction.

Designated Seismic Systems include all systems assigned to Seismic Design Categories C through F, which are either of the following.

Active mechanical or electrical equipment that must remain operable following the design earthquake ground motion.

Components containing hazardous substances and are assigned a Component Importance Factor of 1.5.

        - Special Certification of Designated Seismic Systems: Provide special certification for all Designated Seismic Systems assigned to Seismic Design Categories C through F. Designated Seismic Systems include the following:

          - All active nonstructural mechanical equipment that must remain operable following the design earthquake ground motion. This equipment is assigned an Importance Factor greater than 1.0.

          - Components with hazardous substances and assigned an Importance Factor of 1.5.

        - Provide Special Certification of Designated Seismic Systems.

          - Provide manufacturer's written certification that all designated active mechanical seismic systems will remain operable following the design earthquake. Certification must be based on requirements of ASCE/SEI 7 and ANSI/AHRI 1270 (I-P) or ANSI/AHRI 1271 (SI), including shake table testing as per ICC-ES AC156 or a similar nationally recognized testing standard procedure acceptable to authorities having jurisdiction or experience data as permitted by ASCE/SEI 7.

          - Provide manufacturer's written certification that components with hazardous contents maintain containment following the design earthquake by methods required in ASCE/SEI 7.

          - Submit evidence demonstrating compliance with these requirements for approval to authorities having jurisdiction after review and acceptance by a licensed professional engineer.

            - Active electrical designated seismic systems are those which have parts that rotate, move mechanically, or are energized during operation unless they are considered rugged.

            - Electrical components that contain motors of greater than 10 hp or have a thermal exchange greater than 200 MBH are not rugged.

            - Electrical conduit and buss duct are not active and do not require AC 156 shake table testing.

            - Electrical active designated seismic systems for which experience data for seismic qualification that is acceptable to authorities have jurisdiction does not require AC 156 shake table testing.

Retain subparagraph below only if Designated Seismic Systems are not scheduled. If a schedule is not being used, all Designated Seismic Systems must be listed below. See "Special Certification Requirements for Active Designated Seismic Systems" paragraph in the Evaluations for more information and a list of potential designated systems.

          - The following electrical systems and components are Designated Seismic Systems and require written special certification of seismic qualification by manufacturer;

            - <Insert list>.

      - CLOSEOUT SUBMITTALS

Retain this article for restrained air-spring isolators.

        - Operation and Maintenance Data: For [air-spring mounts] [and] [restrained-air-spring mounts] to include in operation and maintenance manuals.

      - QUALITY ASSURANCE

If an independent testing agency is required, see Section 014000 "Quality Requirements" for general testing and inspecting agency qualification requirements. If additional control is needed, retain "Testing Agency Qualifications" Paragraph below to specify 29 CFR 1910.7. 29 CFR 1910.7 defines "NRTL" (nationally recognized testing laboratory) as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that comply with certain OSHA criteria.

Retain "Testing Agency Qualifications" Paragraph if Contractor selects testing agency, or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.

        - Testing Agency Qualifications: An independent agency, with the experience and capability to conduct the testing indicated, that is an NRTL as defined by OSHA in 29 CFR 1910.7 and that is acceptable to authorities having jurisdiction.

        - Comply with seismic-restraint[, and wind-load] requirements of all applicable codes and authorities having jurisdiction unless requirements in this Section are more stringent.

        - Comply with requirements of [ASCE 7-05 for 2009 IBC] [ASCE/SEI 7-10 including Supplement No. 1 for 2012 IBC] [ASCE/SEI 7-10 including Supplement No. 1 for 2015 IBC] [ASCE/SEI 7-16 for 2018 IBC] <Insert ASCE/SEI 7 edition> for anchorage to concrete, including the effects of prying, unless requirements of the applicable edition of the IBC or this Section are more stringent.

Retain first subparagraph below if ASCE/SEI 7-05 is selected in last paragraph above.

          - Anchorage to concrete or masonry shall be proportioned to carry 1.3 times the calculated seismic load.

Retain first subparagraph below if ASCE/SEI 7-10 is selected in last paragraph above.

          - Overstrength value for determining concrete anchor capacity in ASCE/SEI 7-10, Supplement No. 1, need not be taken as greater than 2.0.

Retain first subparagraph below if ASCE/SEI 7-16 is selected in last paragraph above.

        - Do not use power actuated fasteners in concrete or steel for hanging or bracing in Seismic Design Categories D, E, or F, or in masonry in any Seismic Design Category, unless approved for seismic loading.

        - Friction Clips:

Retain first subparagraph below if ASCE/SEI 7-05 is selected.

          - Component attachments shall be bolted, welded, or otherwise positively fastened without consideration of friction resistance resulting from the effects of gravity. Friction clips (C-type clamps) shall not be used for anchorage attachment.

Retain subparagraph below if ASCE/SEI 7-10 or ASCE/SEI 7-16 is selected.

          - Component attachments shall be bolted, welded or otherwise positively fastened without consideration of friction resistance resulting from the effects of gravity. Friction clips (C-Type beam clamps) shall not be used in Seismic Design Categories D, E, or F to support permanent loads in addition to seismic loads. C-type clamps are permitted for fastening 156 hangers, when they are equipped with retaining straps, equivalent to those specified in NFPA 13, and locknuts are provided to prevent loosening of threaded connections.

Retain "Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

        - Welding Qualifications: Qualify procedures and personnel in accordance with AWS D1.1/D1.1M, "Structural Welding Code - Steel."

        - Comply with requirements of [ASCE/SEI 19-96 for 2009 IBC] [ASCE/SEI 19-10 for 2012 IBC] [ASCE/SEI 19-10 for 2015 IBC] [ASCE/SEI 19-16 for 2018 IBC] <Insert ASCE/SEI 19 edition> for steel cable assemblies used for seismic restraints-cable type.

        - Seismic-restraint devices shall have load ratings based on testing conducted in accordance with IBC referenced standards and listed by a nationally recognized third party that requires periodic follow-up inspections and a has a listing directory available to the public. Third-party listing shall be by [ICC-ES Product Listing] [UL Product Listing] [FM Approvals] [an evaluation service member of ICC-ES] [an agency acceptable to authorities having jurisdiction].

        - Calculations (including combining shear and tensile loads) to support seismic-restraint designs must be signed and sealed by a qualified professional engineer.

        - Consequential Damage: Provide additional seismic restraints for suspended electrical components or anchorage of floor-, roof-, or wall-mounted electrical components so that failure of a non-essential or essential electrical component will not cause failure of any other essential architectural, mechanical, or electrical building component

        - Fire/Smoke Resistance: Seismic[ and wind-load]-restraint devices that are not constructed of ferrous metals shall comply with IMC 602, maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested by an NRTL in accordance with ASTM E84 or UL 723, and be so labeled.

        - Comply with NFPA 70.

- PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

See the Evaluations for more detailed information about controlling vibration, additional information on products described in this Section, illustrations, selection guides, and supplements to equipment schedules.

Coordinate specifications for products in this Section with structural engineer and with Drawings.

      - PERFORMANCE REQUIREMENTS

        - Building ["Occupancy Category" for 2009 IBC] ["Risk Category" for 2012, 2015, or 2018 IBC], Category [I] [II] [III] [IV].

        - Site Class as Defined in ASCE/SEI 7: [A] [B] [C] [D] [E] [F].

        - Seismic design shall be based on the methods presented in [ASCE 7-05] [ASCE/SEI 7-10] [ASCE/SEI 7-16].

        - Horizontal Seismic Design Force: Electrical components shall be designed to resist horizontal earthquake force (Fp), as defined in ASCE/SEI 7, applied at the center of gravity of the component and shall consider both upward and downward vertical forces.

        - Vertical Seismic Design Force: Electrical components shall be designed to resist both upward and downward vertical forces resulting from the application of the horizontal seismic design force plus a concurrent vertical force equal to 0.2 SDSD, as defined in ASCE/SEI 7.

        - Select appropriate seismic coefficients from ASCE/SEI 7, Table 13.6-1.

Retain first paragraph below if using ASCE/SEI 7-05.

        - Exceptions to the Seismic Protection Requirements of this Section for Electrical Components Based on Component Importance Factor (Ip) and Seismic Design Category: The following electrical components are exempt from seismic design requirements of ASCE/SEI 7-05.

          - All electrical components in Seismic Category A or B.

          - Electrical components in Seismic Design Category C where the Component Importance Factor (Ip) equals 1.0.

          - Electrical components in Seismic Design Category D, E, or F where the Component Importance Factor (Ip) equals 1.0 and one of the following:

            - Flexible connections between the components and associated ductwork, piping, or conduit are provided.

            - Components are mounted at 4 ft. (1.22 m) or less above a floor level and weigh 400 lb (1780 N) or less.

          - Electrical components in Seismic Design Category D, E, or F where the Component Importance Factor (Ip) equals 1.0 and the following:

            - Flexible connections between the components and associated duct work, piping, and conduits are provided.

            - Components weigh 20 lb (89 N) or less or, for distribution systems, weigh 5 lb/ft. (73 N/m) or less.

Retain first paragraph below if using ASCE/SEI 7-10.

        - Exceptions to the Seismic Protection Requirements of this Section for Electrical Components based on Component Importance Factor (Ip) and Seismic Design Category: The following electrical components are exempt from seismic design requirements of ASCE/SEI 7-10.

          - Electrical components in Seismic Design Category A or B.

          - Electrical components in Seismic Design Category C where the Component Importance Factor (Ip) equals 1.0.

          - Electrical components in Seismic Design Category D, E, or F where all of the following apply

            - The Component Importance Factor (Ip) equals 1.0.

            - Component is positively attached to the structure.

            - Flexible connections are provided between the component and associated ductwork, piping and conduit, and the component is one of the following:

              - Weighs 400 lb (1780 N) or less and has a center of mass located 4 ft. (1.22 m) or less above the adjacent floor level.

              - Weighs 20 lb (89 N) or less or, in the case of a distributed system, 5 lb/ft. (73 N/m) or less.

Retain first paragraph below if using ASCE/SEI 7-16.

        - Exceptions to the Seismic Protection Requirements of this Section for Electrical Components Based on Component Importance Factor (Ip) and Seismic Design Category: The following electrical components are exempt from seismic design requirements of ASCE/SEI 7-16.

          - Electrical components in Seismic Design Category A or B.

          - Electrical components in Seismic Design Category C provided that one of the following:

            - The Component Importance Factor (Ip) equals 1.0 and the component is positively attached to the structure.

            - Component weighs 20 lb (89 N) or less, or where the component is a distribution system (pipe, duct, etc.) weighing 5 lb/ft. (73 N/m) or less.

          - Electrical components in Seismic Design Category D, E, or F where the components are positively attached to the structure provided that one of the following:

            - Component weighs 400 lb (1779 N) or less, the component center of mass is 4 ft. (1220 mm) or less above the floor; flexible connections are provided between the component and any associated ductwork, piping or conduit, and the Component Importance Factor (Ip) equals 1.0.

            - Component weighs 20 lb (89 N) or less, or where the component is a distribution system (pipe, duct, conduit, etc.) weighing 5 lb/ft. (73 N/m) or less.

Retain first subparagraph below if using ASCE/SEI 7-05.

          - Exceptions Based on Component Size or Method of Attachment: The following electrical components are exempt from seismic design requirements of this Section:

            - Light fixtures, lighted signs, and ceiling fans not connected to ducts or piping where all of the following apply:

              - Components supported by chains or otherwise suspended from the structure.

              - The design load is be equal to 1.4 times the operating weight acting down with a simultaneous horizontal load equal to 1.4 times the operating weight and applied in the direction that results in the most critical loading.

              - Consequential Damage per Section 1.7 Paragraph J will not result.

              - Connection to the structure allows a 360-degree range of motion in the horizontal plane.

Retain first subparagraph below is using ASCE/SEI 7-10.

          - Exceptions Based on Component Size or Method of Attachment: The following electrical components are exempt from seismic design requirements of this Section:

            - Light fixtures, lighted signs, and ceiling fans not connected to ducts or piping, which are supported by chains or otherwise suspended from the structure provided they meet all of the following criteria:

              - Components supported by chains or otherwise suspended from the structure.

              - The design load is be equal to 1.4 times the operating weight acting down with a simultaneous horizontal load equal to 1.4 times the operating weight and applied in the direction that results in the most critical loading.

              - Consequential Damage per Section 1.7 Paragraph J will not result.

              - Connection to the structure allows a 360-degree range of motion in the horizontal plane.

            - Conduit, cable tray, and other electrical distribution systems (raceways) where one of the following:

              - Trapeze assemblies are used to support raceways and the total weight of the raceway supported by trapeze assemblies is less than 10 lb/ft. (146 N/m).

              - Raceway is supported by hangers and each hanger in the raceway run is 12 inches (305 mm) or less in length from the raceway support point to the supporting structure. Where rod hangers are used, they shall be equipped with swivels to prevent inelastic bending in the rod.

              - Design for the seismic forces and relative displacements of Section 13.3 shall not be required for conduit, regardless of the value of Ip, where the conduit is less than 2.5 inch (64 mm) trade size.

Retain first subparagraph below when using ASCE/SEI 7-16.

          - Exceptions Based on Component Size or Method of Attachment: The following electrical components are exempt from seismic design requirements of this Section:

            - Light fixtures, lighted signs, and ceiling fans not connected to ducts or piping, which are supported by chains or otherwise suspended from the structure provided they meet all of the following criteria:

              - Components supported by chains or otherwise suspended from the structure.

              - The design load is be equal to 1.4 times the operating weight acting down with a simultaneous horizontal load equal to 1.4 times the operating weight and applied in the direction that results in the most critical loading.

              - Consequential Damage per Section 1.7 Paragraph J will not result.

              - Connection to the structure allows a 360-degree range of motion in the horizontal plane.

          - Conduit, cable tray, and other electrical distribution systems (raceways) with Ip, = 1.0 where positively attached to the structure and have flexible connections to associated equipment and one of the following apply:

            - Trapeze supports using 3/8-inch- (13 mm-) diameter rod hangers not exceeding 12 inches (305 mm) in length from the trapeze support to the point of connection to the structure and the total weight on any single trapeze is less than 100 lb (445 N).

            - Trapeze supports using 1/2-inch- (10 mm-) diameter rod hangers not exceeding 12 inches (305 mm) in length from the trapeze support to the point of connection to the structure and the total weight on any single trapeze is less than 200 lb (890 N), or

            - Trapeze supports using 1/2-inch- (13 mm-) diameter rod hangers not exceeding 24 inches (610 mm) in length from the trapeze support to the point of connection to the structure and the total weight on any single trapeze is less than 100 lb (445 N).

            - Cable tray, or raceway supported by individual rod hangers 3/8 or 1/2 inch- (10  or 13 mm-) diameter, and each hanger in the raceway run is 12 inches (305 mm) or less in length from the conduit, cable tray, or raceway support point connection to the supporting structure, and the total weight supported by any single rod is 50 lb (220 N) or less.

          - Conduit is less than 2.5 inch (64 mm) trade size.

        - Seismic-Restraint Loading:

See the Evaluations for a discussion on seismic-restraint capacities and rating services.

          - Load ratings, features, and applications shall be as defined in ICC-ES Product Listings, UL Product Listings, ICC-ES Evaluation Reports, OSHPD, or an agency acceptable to authorities having jurisdiction.

            - Load Ratings for seismic restraint components shall include a minimum safety factor of 2.2.

          - Standard supports or proprietary supports shall be designed by load rating or for the calculated seismic forces.

          - Electrical component supports, such as structural members, braces, frames, skirts, legs, saddles, pedestals, cables, guys, stays, snubbers, tethers, and elements forged or cast into a mechanical component, shall be designed for the seismic forces and displacements, including displacement between component supports.

          - The means by which supports are attached to the component, except where cast or forged into the component, including the region of support engagement to the component wall where Ip equals 1.5, shall be designed to accommodate the seismic forces and displacements and to maintain support engagement.

          - The materials comprising supports and the means of attachment to the component, including weak-axis bending of cold-formed steel supports, shall be constructed of materials suitable for the application, including the effects of service conditions and shall be in compliance with a nationally recognized standard.

          - Reinforcement shall be provided at bolted connections through sheet metal equipment housings as required to transfer seismic loads from the equipment to the structure.

          - The design force shall be taken as 2Fp for vibration isolated equipment, if the nominal clearance (air gap) between the equipment support frame and restraint is greater than 0.25 inch (6 mm).

          - Electrical components with Ip greater than 1.0 shall be designed for the seismic forces and relative displacements in this Section and the following additional requirements:

            - Provision shall be made to eliminate seismic impact between components.

            - Loads imposed on the components by attached utility or service lines that are attached to separate structures shall be evaluated.

            - Batteries on racks shall have wrap-around restraints to ensure that batteries will not fall from the rack. Spacers shall be used between restraints and cells to prevent damage to cases and racks shall be evaluated for sufficient lateral load capacity.

            - Internal coils of dry type transformers shall be positively attached to their supporting substructure within the transformer enclosure.

            - Electrical control panels, computer equipment, and other items with slide-out components shall have a latching mechanism to hold the components in place.

            - Electrical cabinet design shall comply with applicable NEMA standards. Cutouts in the lower shear panel that have not been made by manufacturer and reduce significantly the strength of the cabinet shall be specifically evaluated.

            - Attachments for additional external items weighing more than 100 lb (445 N) shall be specifically evaluated if not provided by manufacturer.

            - Where conduit, cable trays, or similar electrical distribution components are attached to structures that could displace relative to one another and for isolated structures where such components cross the isolation interface, components shall be designed to accommodate the seismic relative displacements defined in ASCE/SEI 7, Section 13.3.2.

Retain first subparagraph below when using ASCE/SEI 7-05.

          - Supports for electrical distribution components shall be designed for the seismic forces and relative displacements defined in this Section if any of the following conditions apply:

            - Ip is equal to 1.5 and conduit diameter is greater than 2.5 inch (64 mm) trade size.

            - Trapeze assemblies supporting conduit, bus ducts or cable trays where Ip is equal to 1.5 and the total weight of the bus duct, cable tray, or conduit supported by trapeze assemblies exceeds 10 lb/ft. (146 N/m).

            - Supports are cantilevered up from the floor.

            - Supports include bracing to limit deflection.

            - Supports are constructed as rigid welded frames.

            - Attachments into concrete use non-expanding insets, power-actuated fasteners, or cast-iron embedments.

            - Attachments use spot welds, plug welds, or minimum size welds as defined by AISC.

          - Elevators operating with a speed of 150 ft./min (46 m/min) or greater shall be provided with seismic switches that provide an electrical signal indicating that structural motions are of such a magnitude that the operation of elevators may be impaired. The seismic switch shall be located at or above the highest floor serviced by the elevators. The seismic switch shall have two horizontal perpendicular axes of sensitivity. Its trigger level shall be set to 30 percent of the acceleration of gravity. Upon activation of the seismic switch, elevator operations shall comply with requirements of ASME A17.1, except the following:

            - In facilities where the loss of the use of an elevator is a life-safety issue, the elevator shall only be used after the seismic switch has triggered provided that the elevator shall operate no faster than the service speed and the elevator is operated from top to bottom and back to top to verify that it is operable, before the elevator is occupied.

Retain first subparagraph below when using ASCE/SEI 7-10.

          - Conduit, cable tray, and other electrical distribution systems (raceways) shall be designed for seismic forces and seismic relative displacements required in this Section. Conduit greater than 2.5 inch (64 mm) trade size and attached to panels, cabinets, or other equipment shall be provided with flexible connections or designed for seismic forces and seismic relative displacements as required in this Section.

          - Elevators operating with a speed of 150 ft/min (46 m/min) or greater shall be provided with seismic switches that provide an electrical signal indicating that structural motions are of such a magnitude that the operation of elevators may be impaired. Seismic switches in accordance with Section 8.4.10.1.2 of ASME A17.1 shall be deemed to comply with requirements of this Section.

            - In cases where seismic switches cannot be located near a column in accordance with ASME A17.1, they shall have two horizontal axes of sensitivity and have a trigger level set to 20 percent of the acceleration of gravity where located at or near the base of the structure and 50 percent of the acceleration of gravity in all other locations.

            - Upon activation of the seismic switch, elevator operations shall comply with requirements of ASME A17.1, except the following:

              - In facilities where the loss of the use of an elevator is a life-safety issue, the elevator shall only be used after the seismic switch has triggered provided that the elevator shall operate no faster than the service speed and the elevator is operated from top to bottom and back to top to verify that it is operable, before the elevator is occupied.

Retain first subparagraph below when using ASCE/SEI 7-16.

          - Conduit, cable tray, and other electrical distribution systems (raceways) shall be designed for seismic forces and seismic relative displacements required in this Section. Conduit greater than 2.5 inch (64 mm) trade size and attached to panels, cabinets, or other equipment shall be provided with flexible connections or designed for seismic forces and seismic relative displacements as required in this Section.

          - Design for the displacements across seismic joints shall be required for conduit, cable trays, and raceways with Ip = 1.5 without consideration of conduit size.

          - Trapezes that support a combination of distribution systems (electrical conduit, raceway, duct, piping, etc.) shall be designed for the aggregate weight of the supported system, using the most restrictive requirements for the supported distribution systems. If any distribution system on the trapeze is not exempted, the trapeze shall be braced.

          - Elevators operating with a speed of 150 ft./min (46 m/min) or greater shall be provided with seismic switches that provide an electrical signal indicating that structural motions are of such a magnitude that the operation of elevators may be impaired. Seismic switches in accordance with Section 8.4.10.1.2 of ASME A17.1 shall be deemed to comply with requirements of this Section.

            - In cases where seismic switches cannot be located near a column in accordance with ASME A17.1, they shall have two horizontal axes of sensitivity and have a trigger level set to 20 percent of the acceleration of gravity where located at or near the base of the structure and 50 percent of the acceleration of gravity in all other locations.

            - Upon activation of the seismic switch, elevator operations shall comply with requirements of ASME A17.1, except the following:

              - In facilities where the loss of the use of an elevator is a life-safety issue, the elevator shall only be used after the seismic switch has triggered provided that the elevator shall operate no faster than the service speed and the elevator is operated from top to bottom and back to top to verify that it is operable, before the elevator is occupied.

          - Rooftop solar panels and their attachments shall be designed shall be designed for the seismic forces and relative displacements in this Section and the following additional requirements:

            - Ballasted solar panels without positive direct attachment to the roof structure are permitted on Risk Category I, II, and III structures six stories or fewer in height and having a maximum roof slope equal to or less than 1 in 20, provided that they comply with the following:

              - The height of the center of mass of any panel above the roof surface is less than half the least spacing in plan of the panel supports, but in no case greater than 3 ft. (0.9 m).

              - Each panel is designed to accommodate without impact, instability, or loss of support a seismic displacement, δmpv, of the panel relative to any roof edge or offset and any other curb or obstruction to sliding on the roof surface where δmpv is determined in accordance with ASCE 7-16 Eq. 13.6-1 but is not taken as less than 2 ft. (1.2 m). The minimum separation between adjacent unattached panels shall be taken as 0.5δmpv. Signage or roof markings (e.g., yellow stripes) shall be provided delineating the area around the panel that must be kept free of obstructions. Alternatively, δmpv may be determined by shake table testing or nonlinear response history analysis, whereby the value of δmpv shall not be taken as less than 80 percent of the value given by ASCE 7-16 Eq. 13.6-1, unless independent peer review is conducted in accordance with ASCE 7-16 Section 1.3.1.3.4.

              - Each panel is interconnected to resist a horizontal force of 0.2SDSWpi, across any section cut by a vertical plane, where Wpi is the weight of the smaller of the two portions.

              - Panel framing and supports are designed for a seismic force path from the center of mass of each component to locations of friction resistance equal to the lesser of Fp from ASCE 7-16 Section 13.3.1 and 0.6Wp, where Wp is the weight of each component.

              - All electrical cables leading from a panel to another panel or to another roof object are designed to accommodate, without rupture or distress, differential movements between cable connection points of 1.0δmpv, with consideration given to torsional movement of the panel and its possible impingement on the electrical cables.

              - All edges and offsets of roof surfaces on which panels are placed are bounded by a curb or parapet not less than 12 in. (0.3 m) in height and designed to resist a concentrated load applied at the probable points of impact between the curb or parapet and the panel of not less than 0.2 SDS times the weight of the panel. Alternatively, a panel may be placed so that all parts of the panel are a minimum of 2.0 δmpv, but not less than 4 ft. (1.22 m), from any roof edge or offset.

              - Where justified by testing and analysis, the maximum roof slope for structures assigned to Seismic Design Categories C and D shall be permitted to be 1 in 12 provided that independent peer review is conducted in accordance with ASCE 7-16 Section 1.3.1.3.4.

Retain "Wind-Restraint Loading" Paragraph below for outdoor equipment.

        - Wind-Restraint Loading:

Obtain values for items in subparagraphs below from Project structural engineer or from ASCE/SEI 7.

          - Basic Wind Speed: As defined by wind speed maps in [ASCE/SEI 7-16, Ch. 26] [ASCE/SEI 7-10, Ch. 26] [ASCE 7-05, Ch. 6]. Wind Hazard Map <Insert mph (m/s)> at 33 ft. (10 m) above ground for Exposure Category C. <Insert value>.

          - Minimum 10 lb/sq. ft. (48.8 kg/sq. m) multiplied by maximum area of electrical component projected on vertical plane normal to wind direction, and 45 degrees either side of normal.

          - Perform wind-loading calculations in accordance with ASCE/SEI 7.

      - ELASTOMERIC ISOLATION PADS

Copy "Elastomeric Isolation Pads CSBRP" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric isolation pads depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation pad on the same Project.

Insert drawing designation. Use these designations on Drawings to identify each product.

For information on nVent's "CADDY Elastomeric Isolation Pads," see http://www.vimco.biz/filecabinet/vimco/Literature/P-2201.pdf.

        - Elastomeric Isolation Pads CSBRP: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY Elastomeric Isolation Pads or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Fabrication: Single or multiple layers of sufficient durometer stiffness for uniform loading over pad area.

          - Size: Factory or field cut to match requirements of supported equipment.

Verify availability of various pad materials and their properties with manufacturers.

          - Pad Material: Oil and water resistant with elastomeric properties. [Neoprene] [Silicone] rubber.

          - Surface Pattern: [Smooth] [Ribbed] [Waffle] pattern.

Retain first subparagraph below if pad is infused with synthetic fibers.

          - Infused nonwoven cotton or synthetic fibers.

Retain first subparagraph below if galvanized-steel baseplates are adhered to the isolation pad to facilitate load distribution.

          - Load-bearing metal plates adhered to pads.

Retain "Sandwich-Core Material" Subparagraph below if pad has a sandwich-core material.

Copy "Sandwich-Core Material" Subparagraph and re-edit for each sandwich-core material. Core materials may not be elastomeric. See the "Elastomeric Isolation Pads" Article in the Evaluations for more information.

          - Sandwich-Core Material: [Resilient] [and] [elastomeric] <Insert compound>.

Retain "Surface Pattern" Subparagraph below if the sandwich-core material has a surface pattern.

            - Surface Pattern: [Smooth] [Ribbed] [Waffle] pattern.

Retain subparagraph below if pad is infused with synthetic fibers.

            - Infused nonwoven cotton or synthetic fibers.

      - HOUSED-SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators in Two-Part Telescoping Housing CSBSSM" Paragraph below and re-edit for each product.

The configuration and materials of housed-spring isolators depend on the equipment being supported. It is possible to have more than one type of housed-spring isolator on same Project.

Insert drawing designation. Use these designations on Drawings to identify each product.

For information on nVent's "CADDY Housed-Spring Isolators," see http://www.vimco.biz/filecabinet/vimco/Literature/S-3100-01.pdf.

        - Freestanding, Laterally Stable, Open-Spring Isolators in Two-Part Telescoping Housing CSBSSM: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY Housed-Spring Isolators or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

          - Minimum Additional Travel: 50 percent of the required deflection at rated load.

          - Lateral Stiffness: More than 80 percent of rated vertical stiffness.

          - Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

          - Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators.

            - Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

            - Top housing with [attachment and leveling bolt] [threaded mounting holes and internal leveling device] [elastomeric pad].

      - SPRING ISOLATORS

Copy "Freestanding, Laterally Stable, Open-Spring Isolators with Vertical-Limit Stop Restraint CSBOSM" Paragraph below and re-edit for each product.

The configuration and materials of restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of restrained-spring isolator on same Project.

Insert drawing designation. Use these designations on Drawings to identify each product.

For information on nVent's "CADDY Restrained-Spring Isolators," see http://www.vimco.biz/filecabinet/vimco/Literature/S-2030-01.pdf.

        - Freestanding, Laterally Stable, Open-Spring Isolators with Vertical-Limit Stop Restraint CSBOSM: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY Restrained-Spring Isolators or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Housing: Steel housing with vertical-limit stops to prevent spring extension due to weight being removed.

            - Base with holes for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

            - Top plate with [threaded mounting holes] [elastomeric pad].

            - Internal leveling bolt that acts as blocking during installation.

          - Restraint: Limit stop as required for equipment and authorities having jurisdiction.

          - Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

          - Minimum Additional Travel: 50 percent of the required deflection at rated load.

          - Lateral Stiffness: More than 80 percent of rated vertical stiffness.

          - Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

      - HOUSED-RESTRAINED-SPRING ISOLATORS

Copy "Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing CSBRSM" Paragraph below and re-edit for each product.

The configuration and materials of housed-restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of housed-restrained-spring isolator on same Project.

Insert drawing designation. Use these designations on Drawings to identify each product.

For information on nVent's "CADDY Housed-Restrained-Spring Isolators," see http://www.vimco.biz/filecabinet/vimco/Literature/S-2075-01.pdf.

        - Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing CSBRSM: <Insert drawing designation>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY Housed-Restrained-Spring Isolators or comparable product by one of the following:

            - Vibration Management Corp.

            - Vibration Mountings & Controls, Inc.

            - <Insert manufacturer's name>.

          - Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators. Housings are equipped with [adjustable] [non-adjustable] snubbers to limit vertical movement.

            - Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

            - Threaded top housing with adjustment bolt and cap screw to fasten and level equipment.

          - Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

          - Minimum Additional Travel: 50 percent of the required deflection at rated load.

          - Lateral Stiffness: More than 80 percent of rated vertical stiffness.

          - Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

      - SEISMIC RESTRAINTS – RIGID TYPE

For information on nVent's "CADDY Structure Attachments, Sway Braces and Lateral Telescoping Brace Assemblies for Rigid Seismic Bracing," see https://www.erico.com/category.asp?category=R152.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY Structure Attachments, Sway Braces and Lateral Telescoping Brace Assemblies for Rigid Seismic Bracing or comparable product by one of the following:

          - B-line, an Eaton business.

          - Unistrut; Part of Atkore International.

          - <Insert manufacturer's name>.

        - Description: MFMA-4, shop- or field-fabricated bracing assembly made of ANSI/AISI S100 slotted steel channels, ANSI/ASTM A53 and steel pipe in accordance with NFPA 13 or other rigid steel brace member with accessories for attachment to braced component at one end and to building structure at the other end and other matching components and with corrosion-resistant coating; rated in tension, compression, and torsion forces.

      - SEISMIC RESTRAINTS - CABLE TYPE

For information on nVent's "CADDY Seismic Wire Rope/Cable Bracing" see https://www.erico.com/category.asp?category=R146.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; Size 12 RED, Size 18 WHITE, Size 36 BLUE or Size 48 YELLOW Seismic Wire Rope/Cable Bracing or comparable product by one of the following:

          - Loos & Co.

          - Vibration Mountings & Controls, Inc.

          - <Insert manufacturer's name>.

        - Restraint Cables: [ASTM A1023 galvanized-steel] [ASTM A603 galvanized-steel] [ASTM A492 stainless steel] cables. End connections made of steel assemblies with thimbles, brackets, swivel, and bolts designed for seismic-restraining cable service; with fittings attached by means of poured socket, swaged socket, or mechanical (Flemish eye) loop.

        - Restraint cable assembly and cable fittings must comply with ASCE/SEI 19. All cable assembly fittings shall maintain the minimum breaking force of the cable. U-shaped cable clips and wedge-type end fittings do not comply and are unacceptable.

      - SEISMIC-RESTRAINT ACCESSORIES

For information on nVent's "CADDY Seismic Wire Rope/Cable Bracing Accessories" see https://www.erico.com/category.asp?category=R146.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; Size 12 RED, Size 18 WHITE, Size 36 BLUE, or Size 48 YELLOW Seismic Wire Rope/Cable Spools and Oval Sleeves, URC Universal Restraint Clips, NPC No-Pry Clips, Quick Clip and RS-1 Rod Stiffener Clips, and Structure Attachment and Sway Brace Fittings for 1 to 2 inch (25- to 51-mm) brace members or comparable product by one of the following:

          - Vibration Eliminator Co., Inc.

          - Vibration Mountings & Controls, Inc.

          - <Insert manufacturer's name>.

Retain "Hanger-Rod Stiffener" Paragraph below for strengthening resistance of hanger rods against seismic forces that may cause buckling of rods; delete if detailed on Drawings. Use with either channel- or cable-type bracing assemblies when required to counter seismic forces. Detail fabrication and indicate locations on Drawings.

        - Hanger-Rod Stiffener: Steel tube, steel channel-type strut or steel angle rod stiffener member clamped to hanger rod with rod stiffener clips.

        - Hinged and Swivel Brace Attachments: Multifunctional steel connectors for attaching hangers to [seismic restraints - cable-type] [and] [seismic restraints - rigid-type].

      - POST-INSTALLED CONCRETE ANCHORS IN CONCRETE AND MASONRY

For information on nVent's "CADDY Wedge Expansion Anchors, Screw Anchors," see https://www.erico.com/category.asp?category=R1250.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; CADDY Wedge Expansion Anchors, Screw Anchors or comparable product by one of the following:

          - Powers Fasteners.

          - Simpson Strong-Tie Co., Inc.

          - <Insert manufacturer's name>.

        - Post-installed expansion and undercut anchors in concrete and masonry to be seismically pre-qualified in accordance with ACI 355.2 testing.

        - Post-installed adhesive anchors in concrete and masonry to be seismically pre-qualified in accordance with ACI 355.4 testing.

        - Post-installed anchors in concrete to be designated in accordance with [ACI 318-08 Appendix D for 2009] [ACI 318-11 Appendix D for 2012 IBC] [ACI 318-14 Ch. 17 for 2015 or 2018 IBC].

        - Post-installed anchors in masonry to be designed in accordance with TMS 402.

      - CONCRETE INSERTS

For information on nVent's "CADDY Rod Lock Concrete Inserts," see https://www.erico.com/category.asp?category=R2853.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide CADDY, a brand of nVent; Rod Lock Metal Deck and Plywood Form Inserts or comparable product by one of the following:

          - Powers Fasteners.

          - Simpson Strong-Tie Co., Inc.

          - <Insert manufacturer's name>.

        - Preset Concrete Inserts: To be seismically pre-qualified in accordance with ICC-ES AC446.

- EXECUTION

      - EXAMINATION

        - Examine areas and equipment to receive vibration isolation and seismic-control devices for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in for reinforcement and cast-in-place anchors to verify actual locations before installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - APPLICATIONS

        - Multiple Raceways or Cables: Secure raceways and cables to trapeze member with clamps approved for application by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

Indicate on Drawings, by details, schedules, or a combination of both, the locations where hanger rods for individual raceways, bus duct, cable trays, and hanger rods for trapeze hangers require hanger-rod stiffeners.

        - Hanger-Rod Stiffeners: Install hanger-rod stiffeners where indicated or scheduled on Drawings to receive them and where required to prevent buckling of hanger rods caused by seismic forces.

        - Strength of Support and Seismic-Restraint Assemblies: Where not indicated, select sizes of components so strength is adequate to carry present and future static and seismic loads within specified loading limits.

      - INSTALLATION OF VIBRATION CONTROL[, WIND-LOAD CONTROL,] AND SEISMIC-RESTRAINT DEVICES

        - Provide vibration control devices for systems and equipment where indicated in Equipment Schedules or Vibration Control Devices schedules, where indicated on Drawings, or where the Specifications indicate they are to be installed on specific equipment and systems.

        - Provide seismic restraint[, and wind-load control,] devices for systems and equipment where indicated in Equipment Schedules or Seismic-Restraint Devices Schedules, where indicated on Drawings, where the Specifications indicate they are to be installed on specific equipment and systems, and where required by applicable codes.

        - Installation of vibration isolators must not cause any change of position of equipment, piping, or ductwork resulting in stresses or misalignment.

        - Comply with requirements in Section 077200 "Roof Accessories" for installation of roof curbs, equipment supports, and roof penetration.

        - Equipment and Hanger Restraints:

Indicate type and quantity of snubbers described in first subparagraph below on Drawings or in the Electrical Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

          - Install seismic snubbers on electrical equipment mounted on vibration isolators. Locate snubbers as close as possible to vibration isolators and bolt to equipment base and supporting structure.

          - Install resilient bolt isolation washers on equipment anchor bolts where clearance between anchor and adjacent surface exceeds 0.125 inch (3.2 mm).

          - Install seismic-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] that provides required submittals for component.

          - Space lateral supports a maximum of [40 ft. (12 m)] <Insert dimension> o.c., and longitudinal supports a maximum of [80 ft. (24 m)] <Insert dimension> o.c.

          - Brace a change in direction longer than 12 ft. (3.7 m).

        - Install cables so they do not bend across edges of adjacent equipment or building structure.

        - Attachment to Structure: If specific attachment is not indicated, anchor bracing to structure at flanges of beams, at upper truss chords of bar joists, or at concrete members.

        - Drilled-in Anchors:

          - Identify position of reinforcing steel and other embedded items prior to drilling holes for anchors. Do not damage existing reinforcing or embedded items during coring or drilling. Notify the structural engineer if reinforcing steel or other embedded items are encountered during drilling. Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

          - Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

          - Wedge-Type Anchor Bolts: Protect threads from damage during anchor installation. Heavy-duty sleeve anchors shall be installed with sleeve fully engaged in the structural element to which anchor is to be fastened.

          - Adhesive-Type Anchor Bolts: Clean holes to remove loose material and drilling dust prior to installation of adhesive. Place adhesive in holes proceeding from the bottom of the hole and progressing toward the surface in such a manner as to avoid introduction of air pockets in the adhesive.

          - Set anchors to manufacturer's recommended torque using a torque wrench.

          - Install zinc-coated steel anchors for interior and stainless steel anchors for exterior applications.

      - ACCOMMODATION OF DIFFERENTIAL SEISMIC MOTION

Coordinate this article with Drawings.

        - Flexibility for Differential Movement: Electrical components shall be provided with adequate flexibility to accommodate differential movement between portions of the structure that move differentially, as determined in accordance with ASCE/SEI 7.

      - FIELD QUALITY CONTROL

Retain "Testing Agency" Paragraph below to identify who shall perform tests and inspections. If retaining second option in "Testing Agency" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

        - Manufacturer’s Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

        - Tests and Inspections:

          - Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

            - Provide evidence of recent calibration of test equipment by a testing agency acceptable to authorities having jurisdiction.

            - Schedule test with Owner, through Architect, before connecting anchorage device to restrained component (unless postconnection testing has been approved), and with at least seven days' advance notice.

            - Obtain Architect's approval before transmitting test loads to structure. Provide temporary load-spreading members.

            - Test at least [four] <Insert number> of each type and size of installed anchors and fasteners selected by Architect.

            - Test to 90 percent of rated proof load of device.

            - Measure isolator resistant clearance.

            - Measure Isolator deflection.

            - Verify snubber minimum clearances.

        - Remove and replace malfunctioning units and retest as specified above.

        - Prepare test and inspection reports.

      - ADJUSTING

        - Adjust isolators after piping system is at operating weight.

        - Adjust limit stops on restrained-spring isolators to mount equipment at normal operating height. After equipment installation is complete, adjust limit stops so they are out of contact during normal operation.

END OF SECTION 260548.16